## ProjectDocumentation
Project Name:
Application Name:
Project Description:
Project Owner:
Spec FAQ link: | http://cern.ch/UNICOS-SpecFAQ
Object Descriptions link: | http://cern.ch/UNICOS-ObjectDescription
Spec Changes:
Date | User | Comments | Version | HTML link
0

## SpecDoc
AttributeFamily | AttributeName | HelpCategory | HelpDescription
DeviceDocumentation | Description | Description | Description of the device.
DeviceDocumentation | Description | Usage | Used in the SCADA layer in the device faceplate
DeviceDocumentation | Description | DependentAttributes
DeviceDocumentation | Description | Constraints | In principle there is no limit to the number of characters used, however a long description may result in display issues at the SCADA level. Forbidden characters: ;
DeviceDocumentation | Electrical Diagram | Description | Reference to the electrical diagram in which the device is represented.
DeviceDocumentation | Electrical Diagram | Usage | Used in the SCADA layer: added to the device description in the device faceplate.
DeviceDocumentation | Electrical Diagram | DependentAttributes
DeviceDocumentation | Electrical Diagram | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
DeviceDocumentation | Remarks | Description | Field used to add relevant information about the device.
DeviceDocumentation | Remarks | Usage | This information is not used in the generation process, it remains only at the specification level for documentation purposes.
DeviceDocumentation | Remarks | DependentAttributes
DeviceDocumentation | Remarks | Constraints | Forbidden characters: ;
DeviceIdentification | Expert Name | Description | Name of the device displayed at the SCADA level. It must be unique. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
DeviceIdentification | Expert Name | Usage | It does not affect to the datapoints names in the SCADA layer.
DeviceIdentification | Expert Name | DependentAttributes | Device Links. The name of the device(s) specified in Device Links *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified in Device Links corresponds to "Name".
DeviceIdentification | Expert Name | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦] Expert Name must be unique.
DeviceIdentification | Name | Description | Name of the device. It must be unique. Max length: - Schneider: 23 - Siemens: Field objects, Controller and PCO: 19; Local: 21; otherwise: 24 Forbidden chars: [: "'@`#$%^&*?!,;=+~(){}<>¦]-., double underscore, and page break
DeviceIdentification | Name | Usage | Name displayed at the SCADA level if "Expert Name" is not specified. This name will appear in the datapoints created in the SCADA layer.
DeviceIdentification | Name | DependentAttributes | Device Links. The name of the device(s) specified in Device Links *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified in Device Links corresponds to "Name".
DeviceIdentification | Name | Constraints | Max length: - Schneider: 23 - Siemens: Field objects, Controller and PCO: 19; Local: 21; otherwise: 24 Forbidden chars: [: "'@`#$%^&*?!,;=+~(){}<>¦]-., double underscore, and page break Name must be unique.
FEDeviceAlarm | Auto Acknowledge | Description | The SCADA automatically performs the alarm acknowledge
FEDeviceAlarm | Auto Acknowledge | Usage | When TRUE, the SCADA automatically acknowledges the alarm at its occurrence. The operator doesn't have to act on this alarm.
FEDeviceAlarm | Auto Acknowledge | DependentAttributes
FEDeviceAlarm | Auto Acknowledge | Constraints | TRUE/FALSE
FEDeviceAlarm | Enable Condition | Description | Enable Condition used to enable all defined alarm thresholds (AuEXX). If blank or "logic", then condition is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT AIOBJECT.IOErrorW) is allowed.
FEDeviceAlarm | Enable Condition | Usage | Enable Condition used to enable all defined alarm thresholds (AuEXX).
FEDeviceAlarm | Enable Condition | DependentAttributes
FEDeviceAlarm | Enable Condition | Constraints | If blank or "logic", then condition is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT AIOBJECT.IOErrorW) is allowed.
FEDeviceAlarm | Multiple Types | Description | Declaration of all types of alarm in the case of a multiple dependent objects. Valid only when FEDeviceAlarm::Type is "Multiple", syntax "AlType,AlType". "AlType" must be one of the following valid alarm types: AL,FS,TS,SI.
FEDeviceAlarm | Multiple Types | Usage | Provide to the SCADA information on the Alarm types when several PCO/field objects are dependent of this Alarm
FEDeviceAlarm | Multiple Types | DependentAttributes | FEDeviceAlarm::Type
FEDeviceAlarm | Multiple Types | Constraints | Valid only when FEDeviceAlarm::Type is "Multiple", syntax "AlType,AlType" "AlType" must be one of the following valid alarm types: AL,FS,TS,SI
FEDeviceAlarm | Type | Description | Definition of the Alarm action in the Process: AL: Alarm; no interlock FS: Full Stop TS: Temporary Stop (until alarm disappears) SI: Start Interlock; block ON mode request Multiple: Several PCO/Field objects depend on Alarm - see Multiple Types.
FEDeviceAlarm | Type | Usage | There are 4 valid alarm types: AL: Alarm; will have no effect on PCO/Field FS: Full Stop; will Stop PCO/Field TS: Temporary Stop; will Stop PCO/Field until it disappears. SI: Start Interlock; will block ON mode request applied to the PCO/Field.
FEDeviceAlarm | Type | DependentAttributes | All PCO/Field object specified in this Instance If "Multiple", then must fill out Multiple Types field
FEDeviceAlarm | Type | Constraints
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | Description | Decrease speed of the set-point (Units/s). Must be positive.
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | Usage
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | DependentAttributes
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | Constraints | Must be positive
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | Description | Increase speed of the set-point (Units/s). Must be positive.
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | Usage
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | DependentAttributes
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | Constraints | Must be positive
FEDeviceEnvironmentInputs | ClockWise Limit | Description | Hardware Feedback limit in clockwise reached
FEDeviceEnvironmentInputs | ClockWise Limit | Usage | Used to compute if the device has reached the limit in the ClockWise direction
FEDeviceEnvironmentInputs | ClockWise Limit | DependentAttributes
FEDeviceEnvironmentInputs | ClockWise Limit | Constraints | Must be a DI
FEDeviceEnvironmentInputs | CounterClockWise Limit | Description | Hardware Feedback limit in CounterClocWise reached
FEDeviceEnvironmentInputs | CounterClockWise Limit | Usage | Used to compute if the device has reached the limit in the CounterClockWise direction
FEDeviceEnvironmentInputs | CounterClockWise Limit | DependentAttributes
FEDeviceEnvironmentInputs | CounterClockWise Limit | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Feedback Analog | Description | Analog Feedback of the actuator. Must be an AI/AIR/AS.
FEDeviceEnvironmentInputs | Feedback Analog | Usage | Used to compare with the internal feedback of the device
FEDeviceEnvironmentInputs | Feedback Analog | DependentAttributes
FEDeviceEnvironmentInputs | Feedback Analog | Constraints | Must be an AI/AIR/AS
FEDeviceEnvironmentInputs | Feedback Off | Description | Feedback Off of the actuator. Must be a DI.
FEDeviceEnvironmentInputs | Feedback Off | Usage | Used to compute the "Off" status of the device
FEDeviceEnvironmentInputs | Feedback Off | DependentAttributes
FEDeviceEnvironmentInputs | Feedback Off | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Feedback On | Description | Feedback On of the actuator. Must be a DI.
FEDeviceEnvironmentInputs | Feedback On | Usage | Used to compute the "On" status of the device
FEDeviceEnvironmentInputs | Feedback On | DependentAttributes
FEDeviceEnvironmentInputs | Feedback On | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Hardware Analog Output | Description | Hardware Local Analog request to the actuator when it is in hardware local mode. Must be an AI/AIR/AS.
FEDeviceEnvironmentInputs | Hardware Analog Output | Usage | Signal able to drive the device in case of hardware local mode.
FEDeviceEnvironmentInputs | Hardware Analog Output | DependentAttributes
FEDeviceEnvironmentInputs | Hardware Analog Output | Constraints | Must be an AI/AIR/AS
FEDeviceEnvironmentInputs | Input | Description | Logic for the Alarm input signal. If blank or "logic", then input is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT DIOBJECT) is allowed.
FEDeviceEnvironmentInputs | Input | Usage | Logic for the Alarm input signal.
FEDeviceEnvironmentInputs | Input | DependentAttributes
FEDeviceEnvironmentInputs | Input | Constraints | If blank or "logic", then input is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT DIOBJECT) is allowed.
FEDeviceEnvironmentInputs | Local Drive | Description | Activation of the Hardware Local Drive. Must be a DI.
FEDeviceEnvironmentInputs | Local Drive | Usage | Signal to put the actuator in Hardware Local Mode
FEDeviceEnvironmentInputs | Local Drive | DependentAttributes
FEDeviceEnvironmentInputs | Local Drive | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Local Off | Description | Local Off Request to the actuator when it is in Hardware Local Mode. Must be a DI.
FEDeviceEnvironmentInputs | Local Off | Usage | Signal to send a Local Off Request to the device
FEDeviceEnvironmentInputs | Local Off | DependentAttributes
FEDeviceEnvironmentInputs | Local Off | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Local On | Description | Local On Request to the actuator when it is in Hardware Local Mode. Must be a DI.
FEDeviceEnvironmentInputs | Local On | Usage | Signal to send a Local On Request to the device
FEDeviceEnvironmentInputs | Local On | DependentAttributes
FEDeviceEnvironmentInputs | Local On | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Measured Value | Description | Process Value to be controlled. Must be an AI/AIR/AS.
FEDeviceEnvironmentInputs | Measured Value | Usage | Enter the name of sensor to be regulated
FEDeviceEnvironmentInputs | Measured Value | DependentAttributes
FEDeviceEnvironmentInputs | Measured Value | Constraints | Must be an AI/AIR/AS
FEDeviceIOConfig | FE Encoding Type | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FE Encoding Type | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FE Encoding Type | DependentAttributes | FEChannel.InterfaceParamX (where X=1-10)
FEDeviceIOConfig | FE Encoding Type | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam1 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam1 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam1 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam1 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam10 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam10 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam10 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam10 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam2 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam2 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam2 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam2 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam3 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam3 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam3 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam3 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam4 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam4 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam4 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam4 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam5 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam5 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam5 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam5 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam6 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam6 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam6 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam6 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam7 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam7 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam7 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam7 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam8 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam8 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam8 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam8 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam9 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam9 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam9 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam9 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceManualRequests | H Warning | Description | Threshold level above which the signal produces a Warning. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | H Warning | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | H Warning | DependentAttributes
FEDeviceManualRequests | H Warning | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | HH Alarm | Description | Threshold level above which the signal produces an Alarm. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | HH Alarm | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | HH Alarm | DependentAttributes
FEDeviceManualRequests | HH Alarm | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | L Warning | Description | Threshold level below which the signal produces a Warning. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | L Warning | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | L Warning | DependentAttributes
FEDeviceManualRequests | L Warning | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | LL Alarm | Description | Threshold level below which the signal produces an Alarm. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | LL Alarm | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | LL Alarm | DependentAttributes
FEDeviceManualRequests | LL Alarm | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | Parameter Limit Off/Closed | Description | Limit below which the actuator status is "Off". Must be between Range Min and Range Max.
FEDeviceManualRequests | Parameter Limit Off/Closed | Usage | Used to compute the "Off" status of the device corresponding to the widget being empty in SCADA.
FEDeviceManualRequests | Parameter Limit Off/Closed | DependentAttributes
FEDeviceManualRequests | Parameter Limit Off/Closed | Constraints | Must be between Range Min and Range Max
FEDeviceManualRequests | Parameter Limit On/Open | Description | Limit above which the actuator status is "On". Must be between Range Min and Range Max.
FEDeviceManualRequests | Parameter Limit On/Open | Usage | Used to compute the "On" status of the device corresponding to the widget being completely filled in SCADA.
FEDeviceManualRequests | Parameter Limit On/Open | DependentAttributes
FEDeviceManualRequests | Parameter Limit On/Open | Constraints | Must be between Range Min and Range Max
FEDeviceOutputs | Analog Process Output | Description | Analog Output connected to the process. Must be an AO or AOR.
FEDeviceOutputs | Analog Process Output | Usage
FEDeviceOutputs | Analog Process Output | DependentAttributes
FEDeviceOutputs | Analog Process Output | Constraints | Must be an AO or AOR
FEDeviceOutputs | ClockWise to Reference Switch | Description | Use the ClockWise LimitSwitch as a Reference Switch. Must be a DO.
FEDeviceOutputs | ClockWise to Reference Switch | Usage | Use the ClockWise Limit Switch as a Reference Switch in old equipment that don't allow to do it directly.
FEDeviceOutputs | ClockWise to Reference Switch | DependentAttributes
FEDeviceOutputs | ClockWise to Reference Switch | Constraints | Must be a DO.
FEDeviceOutputs | Controlled Objects | Description | List of devices to be controlled Must be Analog/Anadig/AnaDO/MFC/Controller
FEDeviceOutputs | Controlled Objects | Usage | Enter name of device to be controlled. If several, separate device names with commas.
FEDeviceOutputs | Controlled Objects | DependentAttributes
FEDeviceOutputs | Controlled Objects | Constraints | Must be Analog/Anadig/AnaDO/MFC/Controller
FEDeviceOutputs | Digital Process Output | Description | Output connected to the process. Must be a DO.
FEDeviceOutputs | Digital Process Output | Usage
FEDeviceOutputs | Digital Process Output | DependentAttributes
FEDeviceOutputs | Digital Process Output | Constraints | Must be a DO
FEDeviceOutputs | Driver Enable | Description | Enables the external Power Unit Driver for the motor.
FEDeviceOutputs | Driver Enable | Usage | Used to power off/on the Driver for doing the reference search without moving.
FEDeviceOutputs | Driver Enable | DependentAttributes
FEDeviceOutputs | Driver Enable | Constraints | Must be a DO.
FEDeviceOutputs | Output Off | Description | Negative Output connected to the process for the Bipolar PWM. Must be a DO.
FEDeviceOutputs | Output Off | Usage
FEDeviceOutputs | Output Off | DependentAttributes | Bipolar PWM must be selected as PWM Mode
FEDeviceOutputs | Output Off | Constraints | Must be a DO
FEDeviceOutputs | Output On | Description | Digital Output connected to the process for the Classic PWM. Positive Output connected to the process for the Bipolar PWM. Must be a DO.
FEDeviceOutputs | Output On | Usage
FEDeviceOutputs | Output On | DependentAttributes
FEDeviceOutputs | Output On | Constraints | Must be a DO
FEDeviceOutputs | Process Output | Description | Output connected to the process. Must be a DO.
FEDeviceOutputs | Process Output | Usage
FEDeviceOutputs | Process Output | DependentAttributes
FEDeviceOutputs | Process Output | Constraints | Must be a DO
FEDeviceOutputs | Process Output Off | Description | Output Off connected to the process. Must be a DO.
FEDeviceOutputs | Process Output Off | Usage | Used when the actuator is driven by 2 DO. Some actuators (rare) have 1 DO to open and 1 DO to close (bistable behavior). This DO closes the device.
FEDeviceOutputs | Process Output Off | DependentAttributes | Process Output must be filled
FEDeviceOutputs | Process Output Off | Constraints | Must be a DO
FEDeviceOutputs | Simulated Reference Switch | Description | Simulate Reference Switch. Must be a DO.
FEDeviceOutputs | Simulated Reference Switch | Usage | Used to simulate Reference Switch in equipment that doesn't have it.
FEDeviceOutputs | Simulated Reference Switch | DependentAttributes
FEDeviceOutputs | Simulated Reference Switch | Constraints | Must be a DO.
FEDeviceOutputs | Valve Order | Description | OnOff object representing a valve located in front of the device. Must be a declared OnOff object.
FEDeviceOutputs | Valve Order | Usage | This valve will be driven by the MFC. It prevents leaks because the MFC cannot be fully hermetic when at minimum flow or closed.
FEDeviceOutputs | Valve Order | DependentAttributes | See corresponding OnOff device
FEDeviceOutputs | Valve Order | Constraints | Must be a declared OnOff object
FEDeviceParameters | Alarm Delay (s) | Description | Time delay applied to the condition that sets an Alarm. Can be a number (>= 0), an object (AS,APAR), or empty (set to 0 by default). If = 0, then no delay.
FEDeviceParameters | Alarm Delay (s) | Usage | Active alarm of a duration lower than this delay are ignored. Filter on spikes in Alarm condition.
FEDeviceParameters | Alarm Delay (s) | DependentAttributes
FEDeviceParameters | Alarm Delay (s) | Constraints | Can be a number (>= 0), an object (AS,APAR), or empty (set to 0 by default). If = 0, then no delay.
FEDeviceParameters | CC0 Max Flow (Unit/time) | Description | Device maximum flow (when fully open) with the fluid corresponding to calibration curve 0. Unit/time defined by the operator. Cannot be null/empty (there must be at least one fluid).
FEDeviceParameters | CC0 Max Flow (Unit/time) | Usage
FEDeviceParameters | CC0 Max Flow (Unit/time) | DependentAttributes
FEDeviceParameters | CC0 Max Flow (Unit/time) | Constraints | Cannot be null/empty (there must be at least one fluid)
FEDeviceParameters | CC1 Max Flow (Unit/time) | Description | Device maximum flow (when fully open) with the fluid corresponding to calibration curve 0. Unit/time defined by the operator. Can be null/empty.
FEDeviceParameters | CC1 Max Flow (Unit/time) | Usage
FEDeviceParameters | CC1 Max Flow (Unit/time) | DependentAttributes
FEDeviceParameters | CC1 Max Flow (Unit/time) | Constraints | Can be null/empty.
FEDeviceParameters | CC2 Max Flow (Unit/time) | Description | Device maximum flow (when fully open) with the fluid corresponding to calibration curve 0. Unit/time defined by the operator. Can be null/empty.
FEDeviceParameters | CC2 Max Flow (Unit/time) | Usage
FEDeviceParameters | CC2 Max Flow (Unit/time) | DependentAttributes
FEDeviceParameters | CC2 Max Flow (Unit/time) | Constraints | Can be null/empty.
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | Description | Time constant of the 1st order filter applied to the Measured Value. Must be larger than the PLC cycle time.
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | Usage | The time filter is applied on the measured value to reduce noise
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | DependentAttributes
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | Constraints | Must be larger than the PLC cycle time
FEDeviceParameters | Controller Parameters::Output Range Max | Description | Output Range Max if different from controlled devices. If empty, take range of the first controlled device.
FEDeviceParameters | Controller Parameters::Output Range Max | Usage | Can be used if split range is performed with the controller
FEDeviceParameters | Controller Parameters::Output Range Max | DependentAttributes
FEDeviceParameters | Controller Parameters::Output Range Max | Constraints
FEDeviceParameters | Controller Parameters::Output Range Min | Description | Output Range Min if different from controlled devices. If empty, take range of the first controlled device.
FEDeviceParameters | Controller Parameters::Output Range Min | Usage | Can be used if split range is performed with the controller
FEDeviceParameters | Controller Parameters::Output Range Min | DependentAttributes
FEDeviceParameters | Controller Parameters::Output Range Min | Constraints
FEDeviceParameters | Controller Parameters::PID Cycle (s) | Description | Cycle time to call the PID algorithm. Must be larger than the PLC cycle time.
FEDeviceParameters | Controller Parameters::PID Cycle (s) | Usage
FEDeviceParameters | Controller Parameters::PID Cycle (s) | DependentAttributes
FEDeviceParameters | Controller Parameters::PID Cycle (s) | Constraints | Must be larger than the PLC cycle time
FEDeviceParameters | Controller Parameters::RA | Description | Reverse Action on the controller
FEDeviceParameters | Controller Parameters::RA | Usage | If TRUE, the Kc parameter will be negative, i.e. if MV > SP, Output will increase. If FALSE (=default), Kc will be positive, i.e. if MV > SP, Output will decrease.
FEDeviceParameters | Controller Parameters::RA | DependentAttributes
FEDeviceParameters | Controller Parameters::RA | Constraints
FEDeviceParameters | Controller Parameters::Scaling Method | Description | Scaling method applied to the PID
FEDeviceParameters | Controller Parameters::Scaling Method | Usage | Input Scaling (1, default): the SP and the MV are scaled. Output 0-100% Input/Output Scaling (2): Same as Input Scaling but Output can be scaled to engineering values (Output Range Min/Max) No Scaling (3): use engineering values. Kc has physical meaning
FEDeviceParameters | Controller Parameters::Scaling Method | DependentAttributes
FEDeviceParameters | Controller Parameters::Scaling Method | Constraints
FEDeviceParameters | Deadband (%) | Description | Deadband applied to the Engineering value at the PLC level.
FEDeviceParameters | Deadband (%) | Usage | The value entered here must be consistent with the resolution of the PLC channel.
FEDeviceParameters | Deadband (%) | DependentAttributes
FEDeviceParameters | Deadband (%) | Constraints | Variations of the Engineering value below the % of the Engineering range will be discarded.
FEDeviceParameters | Deadband Trigger | Description | Deadband value in engineering units to Trigger a new Positioning job
FEDeviceParameters | Deadband Trigger | Usage | Minimum difference between the Actual position and the Commanded position to trigger a new positioning job.
FEDeviceParameters | Deadband Trigger | DependentAttributes
FEDeviceParameters | Deadband Trigger | Constraints | Must be positive
FEDeviceParameters | Default Value | Description | Default value for the parameter
FEDeviceParameters | Default Value | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Value | DependentAttributes
FEDeviceParameters | Default Value | Constraints
FEDeviceParameters | Encoder Type | Description | Type of encoder in use.
FEDeviceParameters | Encoder Type | Usage | Here you can choose between different encoder types.
FEDeviceParameters | Encoder Type | DependentAttributes
FEDeviceParameters | Encoder Type | Constraints
FEDeviceParameters | Filtering Time (s) | Description | First Order Filter applied to the Engineering value at the PLC level.
FEDeviceParameters | Filtering Time (s) | Usage | A first order filter is applied to the engineering value.
FEDeviceParameters | Filtering Time (s) | DependentAttributes
FEDeviceParameters | Filtering Time (s) | Constraints | the filter will absorb the noise of the signal
FEDeviceParameters | Flow Conversion | Description | Scale factor to convert set point and flow values to different units, for display and control purposes. Use this factor when the device works in one physical unit (e.g. l/min) but the operator wants to view in another unit (e.g. l/h)
FEDeviceParameters | Flow Conversion | Usage
FEDeviceParameters | Flow Conversion | DependentAttributes
FEDeviceParameters | Flow Conversion | Constraints | Must be > 0
FEDeviceParameters | Manual Decrease Speed (Unit/s) | Description | Decrease speed of the actuator when user requests a new value from SCADA. Must be positive.
FEDeviceParameters | Manual Decrease Speed (Unit/s) | Usage
FEDeviceParameters | Manual Decrease Speed (Unit/s) | DependentAttributes
FEDeviceParameters | Manual Decrease Speed (Unit/s) | Constraints | Must be positive
FEDeviceParameters | Manual Decrease Step (Unit) | Description | Step amplitude in Unit value when user requests a "decrease value" from SCADA. Must be positive and < (Range Max-Range Min)
FEDeviceParameters | Manual Decrease Step (Unit) | Usage
FEDeviceParameters | Manual Decrease Step (Unit) | DependentAttributes
FEDeviceParameters | Manual Decrease Step (Unit) | Constraints | Must be positive and < (Range Max-Range Min)
FEDeviceParameters | Manual Increase Speed (Unit/s) | Description | Increase speed of the actuator when user requests a new value from SCADA. Must be positive.
FEDeviceParameters | Manual Increase Speed (Unit/s) | Usage
FEDeviceParameters | Manual Increase Speed (Unit/s) | DependentAttributes
FEDeviceParameters | Manual Increase Speed (Unit/s) | Constraints | Must be positive
FEDeviceParameters | Manual Increase Step (Unit) | Description | Step amplitude in Unit value when user requests an "increase value" from SCADA. Must be positive and < (Range Max-Range Min).
FEDeviceParameters | Manual Increase Step (Unit) | Usage
FEDeviceParameters | Manual Increase Step (Unit) | DependentAttributes
FEDeviceParameters | Manual Increase Step (Unit) | Constraints | Must be positive and < (Range Max-Range Min)
FEDeviceParameters | Max Speed | Description | Maximum speed allowed. It has to be between 1 and 254
FEDeviceParameters | Max Speed | Usage | Specifies the maximum speed that the device can move safely.
FEDeviceParameters | Max Speed | DependentAttributes
FEDeviceParameters | Max Speed | Constraints | Must be less than 254
FEDeviceParameters | Maximum Range | Description | Highest Position that the device can reach.
FEDeviceParameters | Maximum Range | Usage | Highest Position that the device can reach.
FEDeviceParameters | Maximum Range | DependentAttributes
FEDeviceParameters | Maximum Range | Constraints | Must be bigger than Minimum Range.
FEDeviceParameters | Minimum Range | Description | Lowest Position that the device can reach.
FEDeviceParameters | Minimum Range | Usage | Lowest position that the device can reach.
FEDeviceParameters | Minimum Range | DependentAttributes
FEDeviceParameters | Minimum Range | Constraints
FEDeviceParameters | Offset | Description | Offset added in engineering units for the conversion between steps and engineering units.
FEDeviceParameters | Offset | Usage
FEDeviceParameters | Offset | DependentAttributes
FEDeviceParameters | Offset | Constraints | Must be positive
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | Constraints
FEDeviceParameters | PWM Parameters::Max Deviation | Description | Maximum amplitude of the PWM output corresponding to a duty cycle of 100% (the 'DO On' remains at One). Must be between Range Min and Range Max.
FEDeviceParameters | PWM Parameters::Max Deviation | Usage
FEDeviceParameters | PWM Parameters::Max Deviation | DependentAttributes
FEDeviceParameters | PWM Parameters::Max Deviation | Constraints | Must be between Range Min and Range Max
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | Description | Minimum pulse duration of the PWM. Must be larger than the PLC cycle time.
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | Usage
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | DependentAttributes
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | Constraints | Must be larger than the PLC cycle time
FEDeviceParameters | PWM Parameters::Time Period (s) | Description | Time Period to generate the Pulse Wave Modulation (PWM). The time period must be larger than the PLC cycle time and larger than the pulse minimum duration.
FEDeviceParameters | PWM Parameters::Time Period (s) | Usage
FEDeviceParameters | PWM Parameters::Time Period (s) | DependentAttributes | PWM Parameters.Minimum Duration (s)
FEDeviceParameters | PWM Parameters::Time Period (s) | Constraints | The time period must be larger than the PLC cycle time and larger than the pulse minimum duration
FEDeviceParameters | ParReg::Constant Time Pulse | Description | Only relevant if object is pulsed (Pulse Duration (s) column is not blank): - if blank/FALSE: output is pulsed until feedback is received - if TRUE: output will always pulse for specified duration, regardless of the feedback
FEDeviceParameters | ParReg::Constant Time Pulse | Usage
FEDeviceParameters | ParReg::Constant Time Pulse | DependentAttributes | Pulse Duration (s)
FEDeviceParameters | ParReg::Constant Time Pulse | Constraints | Only taken into account if Pulse Duration (s) is not blank
FEDeviceParameters | ParReg::Convert ratio to Unit/time | Description | Set this flag to TRUE if the hardware reads flow as a ratio (%) of max flow. If TRUE, all set point and flow values will be converted from % into physical units using the max flow defined in "CCn Max Flow (Unit/time)" attribute.
FEDeviceParameters | ParReg::Convert ratio to Unit/time | Usage
FEDeviceParameters | ParReg::Convert ratio to Unit/time | DependentAttributes | CCn Max Flow (Unit/time)
FEDeviceParameters | ParReg::Convert ratio to Unit/time | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Fail-Safe | Description | Fail Safe position of the actuator
FEDeviceParameters | ParReg::Fail-Safe | Usage | This is the position of the device in case of interlock.
FEDeviceParameters | ParReg::Fail-Safe | DependentAttributes
FEDeviceParameters | ParReg::Fail-Safe | Constraints
FEDeviceParameters | ParReg::Feedback | Description | Enables the use of the Analog Feedback from the potentiometer as Support for positioning, but still open loop.
FEDeviceParameters | ParReg::Feedback | Usage | Activate this option to use the Feedback from the potentiometer as support instead of defining position.
FEDeviceParameters | ParReg::Feedback | DependentAttributes
FEDeviceParameters | ParReg::Feedback | Constraints
FEDeviceParameters | ParReg::Feedback Off | Description | The hardware device does not provide feedback signals. If TRUE, all feedback signals from the hardware will be simulated.
FEDeviceParameters | ParReg::Feedback Off | Usage
FEDeviceParameters | ParReg::Feedback Off | DependentAttributes
FEDeviceParameters | ParReg::Feedback Off | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Full/Empty Animation | Description | Full/Empty Widget Animation type: If Full/Empty, the object is always animated full/empty if active Feedback Off/On is not set. Otherwise, if Full/Half/Empty, the object is only animated half full. For more details, see OnOff object description
FEDeviceParameters | ParReg::Full/Empty Animation | Usage | To always represent the widget as Full or Empty when only one Hardware Feedback is declared.
FEDeviceParameters | ParReg::Full/Empty Animation | DependentAttributes
FEDeviceParameters | ParReg::Full/Empty Animation | Constraints | Full/Empty Animation is applied, when only one Hardware Feedback is declared (PHFOn or PHFOff).
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | Description | The operator cannot act on the control of the Flow totalizer. If TRUE, the flow totalizer is only managed by the process.
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | Usage
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | DependentAttributes
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Description | Strategy to adopt to restart the device after a Full Stop Interlock.
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Usage | FALSE: Device restarts after acknowledge. TRUE only if Full Stop disappeared: Ack+Allow Restart needed (possible only if FS disappeared) TRUE even if Full Stop still active: Ack+Allow Restart needed (possible at any moment)
FEDeviceParameters | ParReg::Manual Restart after Full Stop | DependentAttributes
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Constraints | All devices of the application should have the same "Manual Restart after Full Stop"
FEDeviceParameters | ParReg::Noise Filter | Description | Remove noisy flow measurements for low flow set points. If TRUE noisy flow measurements (< 0.1% of the Max flow) will be suppressed when the valve setpoint is Min or closed.
FEDeviceParameters | ParReg::Noise Filter | Usage
FEDeviceParameters | ParReg::Noise Filter | DependentAttributes | CCn Max Flow (Unit/time)
FEDeviceParameters | ParReg::Noise Filter | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Outputs Maintained | Description | Maintain the output when Range Max is reached.
FEDeviceParameters | ParReg::Outputs Maintained | Usage | TRUE: The process output will remain TRUE when the Range Max is reached. FALSE: The process output will go FALSE when the Range Max is reached.
FEDeviceParameters | ParReg::Outputs Maintained | DependentAttributes
FEDeviceParameters | ParReg::Outputs Maintained | Constraints
FEDeviceParameters | ParReg::PWM Mode | Description | Mode used to generate the Pulse Wave Modulation (PWM).
FEDeviceParameters | ParReg::PWM Mode | Usage | Classic mode uses a single DO. Bipolar mode uses 2 DO (1 DO to go up and 1 DO to go down).
FEDeviceParameters | ParReg::PWM Mode | DependentAttributes | If Bipolar mode is selected, the field "Output Off" must be specified
FEDeviceParameters | ParReg::PWM Mode | Constraints
FEDeviceParameters | ParReg::Position Alarm | Description | If TRUE, set Position Alarm if a Local object has no hardware feedback from its only active feedback signal
FEDeviceParameters | ParReg::Position Alarm | Usage | Position Alarm will display SCADA widget in red in this case and allow user to quickly identify valves which are not in correct position
FEDeviceParameters | ParReg::Position Alarm | DependentAttributes
FEDeviceParameters | ParReg::Position Alarm | Constraints | Position Alarm Animation is applied, when only one Hardware Feedback is declared (PHFOn or PHFOff).
FEDeviceParameters | ParReg::Switches Configuration | Description | Enables the activation of the Feedback ClockWise and CounterClockWise of the object via a hardware sensor connected to the stepper module.
FEDeviceParameters | ParReg::Switches Configuration | Usage | This describes the switches configuration in the physical installation.
FEDeviceParameters | ParReg::Switches Configuration | DependentAttributes
FEDeviceParameters | ParReg::Switches Configuration | Constraints
FEDeviceParameters | Pulse Duration (s) | Description | Pulse duration (s). - if != 0, OnOff output will be pulsed for X seconds. - if blank or =0, output is not pulsed. N.B. Pulse behaviour depends on "Constant Time Pulse" column.
FEDeviceParameters | Pulse Duration (s) | Usage | Determines whether OnOff object is pulsed or not
FEDeviceParameters | Pulse Duration (s) | DependentAttributes | Constant Time Pulse
FEDeviceParameters | Pulse Duration (s) | Constraints
FEDeviceParameters | Range Max | Description | Maximum engineering value of the device.
FEDeviceParameters | Range Max | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Range Max | DependentAttributes
FEDeviceParameters | Range Max | Constraints | The value specified here must be consistent with the format defined in the field "Format".
FEDeviceParameters | Range Min | Description | Minimum engineering value of the device.
FEDeviceParameters | Range Min | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Range Min | DependentAttributes
FEDeviceParameters | Range Min | Constraints | The value specified here must be consistent with the format defined in the field "Format".
FEDeviceParameters | Raw Max | Description | Minimum raw value of the device.
FEDeviceParameters | Raw Max | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Raw Max | DependentAttributes
FEDeviceParameters | Raw Max | Constraints
FEDeviceParameters | Raw Min | Description | Minimum raw value of the device.
FEDeviceParameters | Raw Min | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Raw Min | DependentAttributes
FEDeviceParameters | Raw Min | Constraints
FEDeviceParameters | Reference Position | Description | Position of the Reference Switch in engineering units referenced to the Minimum and Maximum Position.
FEDeviceParameters | Reference Position | Usage | Position of the device after finishing the reference search.
FEDeviceParameters | Reference Position | DependentAttributes
FEDeviceParameters | Reference Position | Constraints
FEDeviceParameters | Scale | Description | Number of Steps to move for one engineering unit.
FEDeviceParameters | Scale | Usage | To calculate the number of steps that the motor will move, the distance is multiplied by this number.
FEDeviceParameters | Scale | DependentAttributes
FEDeviceParameters | Scale | Constraints | Must be positive
FEDeviceParameters | Volume Conversion | Description | Scale factor to convert measured volume to different units. Use this factor when the device works in one physical unit (e.g. l) but the operator wants to view in another unit (e.g. m3). Value 0 should not be applied.
FEDeviceParameters | Volume Conversion | Usage
FEDeviceParameters | Volume Conversion | DependentAttributes
FEDeviceParameters | Volume Conversion | Constraints | Value 0 should not be applied.
FEDeviceParameters | Warning Deadband Value (Unit) | Description | Deadband value to compute the position warning of the device (Discordance). Must be positive.
FEDeviceParameters | Warning Deadband Value (Unit) | Usage | can be a positive number or a parameter
FEDeviceParameters | Warning Deadband Value (Unit) | DependentAttributes
FEDeviceParameters | Warning Deadband Value (Unit) | Constraints | Must be positive
FEDeviceParameters | Warning Time Delay (s) | Description | Delay applied to the Position Alarm when there is a discordance between OutputOrder and Feedback position. Must be positive.
FEDeviceParameters | Warning Time Delay (s) | Usage | can be a positive number or a parameter
FEDeviceParameters | Warning Time Delay (s) | DependentAttributes
FEDeviceParameters | Warning Time Delay (s) | Constraints | Must be positive
FEDeviceVariables | Default PID Parameters::Kc | Description | Default Kc parameter (Gain) of the Controller at the initialization of the PLC. Must be positive. If reverse action, put TRUE in the "Reverse Action" field. If blank, will be set to 1.0 by default.
FEDeviceVariables | Default PID Parameters::Kc | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Kc | DependentAttributes
FEDeviceVariables | Default PID Parameters::Kc | Constraints | Must be positive. If reverse action, put TRUE in the "Reverse Action" field. If blank, will be set to 1.0 by default.
FEDeviceVariables | Default PID Parameters::Out High Limit | Description | Default High Limit for the Controller output at the initialization of the PLC. Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Max.
FEDeviceVariables | Default PID Parameters::Out High Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Out High Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::Out High Limit | Constraints | Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Max
FEDeviceVariables | Default PID Parameters::Out Low Limit | Description | Default Low Limit for the Controller output at the initialization of the PLC. Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Min.
FEDeviceVariables | Default PID Parameters::Out Low Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Out Low Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::Out Low Limit | Constraints | Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Min
FEDeviceVariables | Default PID Parameters::SP High Limit | Description | Default High Limit for the Controller Set-Point at the initialization of the PLC. Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Max of the MV.
FEDeviceVariables | Default PID Parameters::SP High Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::SP High Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::SP High Limit | Constraints | Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Max of the MV
FEDeviceVariables | Default PID Parameters::SP Low Limit | Description | Default Low Limit for the Controller Set-Point at the initialization of the PLC. Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Min of the MV.
FEDeviceVariables | Default PID Parameters::SP Low Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::SP Low Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::SP Low Limit | Constraints | Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Min of the MV
FEDeviceVariables | Default PID Parameters::Setpoint | Description | Default Set-Point of the Controller at the initialization of the PLC. Must be between Range Min and Range Max of the Measured Value. If blank, will be set to 0.0 by default.
FEDeviceVariables | Default PID Parameters::Setpoint | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Setpoint | DependentAttributes
FEDeviceVariables | Default PID Parameters::Setpoint | Constraints | Must be between Range Min and Range Max of the Measured Value. If blank, will be set to 0.0 by default.
FEDeviceVariables | Default PID Parameters::Td | Description | Default Td parameter (Derivative Time) of the Controller at the initialization of the PLC. Must be >= 0. If = 0, then derivative component is removed. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Td | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Td | DependentAttributes
FEDeviceVariables | Default PID Parameters::Td | Constraints | Must be >= 0. If = 0, then derivative component is removed. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Tds | Description | Default Tds parameter (time constant of the 1st order filter on the derivative term) of the Controller at the initialization of the PLC. Must be >= 0. If = 0, then no filtering of the derivative term. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Tds | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Tds | DependentAttributes
FEDeviceVariables | Default PID Parameters::Tds | Constraints | Must be >= 0. If = 0, then no filtering of the derivative term. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Ti | Description | Default Ti parameter (Integration Time) of the Controller at the initialization of the PLC. Must be >= 0. If = 0, then integral component is removed. If blank, will be set to 100.0s by default.
FEDeviceVariables | Default PID Parameters::Ti | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Ti | DependentAttributes
FEDeviceVariables | Default PID Parameters::Ti | Constraints | Must be >= 0. If = 0, then integral component is removed. If blank, will be set to 100.0s by default.
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicSections::BL User Template | Description | Define user template for the Basic Logic
LogicDeviceDefinitions | CustomLogicSections::BL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::BL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::BL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | Description | Define user template for the Common Dependent Object Logic
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::CL User Template | Description | Define user template for the Configuration Logic
LogicDeviceDefinitions | CustomLogicSections::CL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::CL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::CL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Description | Define user template for the Dependent Logic
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::DL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::GL User Template | Description | Define user template for the Global Logic
LogicDeviceDefinitions | CustomLogicSections::GL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::GL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::GL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::IL User Template | Description | Define user template for the Interlock Logic
LogicDeviceDefinitions | CustomLogicSections::IL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::IL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::IL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::INST User Template | Description | Define user template for the instantiation of the PCO
LogicDeviceDefinitions | CustomLogicSections::INST User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::INST User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::INST User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::SL User Template | Description | Define user template for the Sequencer Logic
LogicDeviceDefinitions | CustomLogicSections::SL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::SL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::SL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::TL User Template | Description | Define user template for the Transition Logic
LogicDeviceDefinitions | CustomLogicSections::TL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::TL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::TL User Template | Constraints
LogicDeviceDefinitions | External Master | Description | Master of the device if located in another PLC for WinCCOA.
LogicDeviceDefinitions | External Master | Usage | The external master will give automatic requests to the device from another PLC. To be specified only if master is empty.
LogicDeviceDefinitions | External Master | DependentAttributes
LogicDeviceDefinitions | External Master | Constraints | Must be a single PCO for field objects, controller, or PCO.
LogicDeviceDefinitions | Fast Interlock Type | Description | Type of fast interlock object if necesary
LogicDeviceDefinitions | Fast Interlock Type | Usage | This parameter is used to determinate if the object will be processed in the fast interlock logic
LogicDeviceDefinitions | Fast Interlock Type | DependentAttributes
LogicDeviceDefinitions | Fast Interlock Type | Constraints
LogicDeviceDefinitions | Master | Description | Master of the device (relative to the hierarchy of dependent objects).
LogicDeviceDefinitions | Master | Usage | The master will give automatic requests to the device. The master object will appear in the list of "Device Links" in the device right-click menu.
LogicDeviceDefinitions | Master | DependentAttributes
LogicDeviceDefinitions | Master | Constraints | Must be a single PCO for field objects, controller, or PCO. Must be PCO or field objects for alarms (several masters are allowed in the case of multiple alarms, separated by commas or spaces).
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Description | The SCADA automatically performs the alarm acknowledge
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Usage | When TRUE, the SCADA automatically acknowledges the alarm at its occurrence. The operator doesn't have to act on this alarm.
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | DependentAttributes
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Constraints | TRUE/FALSE
SCADADeviceAlarms | Alarm Config::Level | Description | Classification of the importance of the Alarm
SCADADeviceAlarms | Alarm Config::Level | Usage | Level 0: Information Level 1: Warning Level 2: Alarm Level 3: Safety Alarm
SCADADeviceAlarms | Alarm Config::Level | DependentAttributes
SCADADeviceAlarms | Alarm Config::Level | Constraints
SCADADeviceAlarms | Alarm Config::Masked | Description | Alarm signal is ignored by the SCADA
SCADADeviceAlarms | Alarm Config::Masked | Usage | When TRUE, the Alarm signal is not recorded into the ALARM database
SCADADeviceAlarms | Alarm Config::Masked | DependentAttributes
SCADADeviceAlarms | Alarm Config::Masked | Constraints | TRUE/FALSE
SCADADeviceAlarms | Alarm Config::SMS Category | Description | This Alarm message will follow rules defined in the corresponding SMS User Group (comma-separated list)
SCADADeviceAlarms | Alarm Config::SMS Category | Usage | Defines a specific treatment for each SMS message
SCADADeviceAlarms | Alarm Config::SMS Category | DependentAttributes
SCADADeviceAlarms | Alarm Config::SMS Category | Constraints | The name must correspond to the SMS user group (unProcessAlarm,...)
SCADADeviceAlarms | Alarm Values::High | Description | High Alarm values (comma-separated list of integer values)
SCADADeviceAlarms | Alarm Values::High | Usage | Used to define High Alarm values on a status at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process.
SCADADeviceAlarms | Alarm Values::High | DependentAttributes
SCADADeviceAlarms | Alarm Values::High | Constraints | Must be a list of comma-separated integers.
SCADADeviceAlarms | Alarm Values::Low | Description | Low Alarm values (comma-separated list of integer values)
SCADADeviceAlarms | Alarm Values::Low | Usage | Used to define Low Alarm values on a status at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process.
SCADADeviceAlarms | Alarm Values::Low | DependentAttributes
SCADADeviceAlarms | Alarm Values::Low | Constraints | Must be a list of comma-separated integers.
SCADADeviceAlarms | Alarm Values::Medium | Description | Medium Alarm values (comma-separated list of integer values)
SCADADeviceAlarms | Alarm Values::Medium | Usage | Used to define Medium Alarm values on a status at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process.
SCADADeviceAlarms | Alarm Values::Medium | DependentAttributes
SCADADeviceAlarms | Alarm Values::Medium | Constraints | Must be a list of comma-separated integers.
SCADADeviceAlarms | Alarm Values::Safety | Description | Safety Alarm values (comma-separated list of integer values)
SCADADeviceAlarms | Alarm Values::Safety | Usage | Used to define Safety Alarm values on a status at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process.
SCADADeviceAlarms | Alarm Values::Safety | DependentAttributes
SCADADeviceAlarms | Alarm Values::Safety | Constraints | Must be a list of comma-separated integers.
SCADADeviceAlarms | Analog Thresholds::H Warning | Description | High (H) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::H Warning | Usage | Used to define an H Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::H Warning | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::H Warning | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Description | High High (HH) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Usage | Used to define an HH Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::HH Alarm | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::L Warning | Description | Low (L) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::L Warning | Usage | Used to define an L Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::L Warning | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::L Warning | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Description | Low Low (LL) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Usage | Used to define an LL Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::LL Alarm | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Binary State::Alarm On State | Description | State of the device where the PVSS alert should be triggered. Blank/empty (=default) indicates that there is no PVSS alert.
SCADADeviceAlarms | Binary State::Alarm On State | Usage | This alarm is only used at SCADA level for information and It has no impact on the process.
SCADADeviceAlarms | Binary State::Alarm On State | DependentAttributes
SCADADeviceAlarms | Binary State::Alarm On State | Constraints
SCADADeviceAlarms | Message | Description | Message to display when alarm is set in SCADA
SCADADeviceAlarms | Message | Usage | The message specified here will be displayed in the Alarm List
SCADADeviceAlarms | Message | DependentAttributes
SCADADeviceAlarms | Message | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[:"'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Analog Archive | Description | Name of the analog archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Analog Archive | Usage | The analog values of the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Analog Archive | DependentAttributes
SCADADeviceDataArchiving | Analog Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Archive Mode | Constraints
SCADADeviceDataArchiving | Boolean Archive | Description | Name of the Boolean archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Boolean Archive | Usage | The boolean values of the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Boolean Archive | DependentAttributes
SCADADeviceDataArchiving | Boolean Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the engineering values of the object
SCADADeviceDataArchiving | Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Deadband Type | Constraints
SCADADeviceDataArchiving | Deadband Value | Description | Deadband value for the SCADA archiving of the engineering values of the object Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Deadband Value | Usage
SCADADeviceDataArchiving | Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Event Archive | Description | Name of the event archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Event Archive | Usage | The events generated by the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Event Archive | DependentAttributes
SCADADeviceDataArchiving | Event Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Flow::Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Flow::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Flow::Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Flow::Archive Mode | Constraints
SCADADeviceDataArchiving | Flow::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the Flow.
SCADADeviceDataArchiving | Flow::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Flow::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Flow::Deadband Type | Constraints
SCADADeviceDataArchiving | Flow::Deadband Value | Description | Deadband value for the SCADA archiving of the Flow. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Flow::Deadband Value | Usage
SCADADeviceDataArchiving | Flow::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Flow::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Flow::Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object. Must be positive.
SCADADeviceDataArchiving | Flow::Time Filter (s) | Usage
SCADADeviceDataArchiving | Flow::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Flow::Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | Description | Define the archive action when there is a change on the interlock state. Archive if: Old/New Comparison: value changes
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | Usage | This archive mode is used to archive alarm output state in the PVSS database
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | DependentAttributes
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | Constraints | No, or Old/New Comparison
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | Description | Archive mode of MV and SP. Archive if: Old/New Comparison: value changes Time: value changes after the specified Time Filter Deadband: value < or > specified deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | DependentAttributes | If "Time" is selected, "MV and SP Archiving.Time Filter (s)" must be filled If "Deadband" is selected: "MV and SP Archiving.Deadband Type" and "MV and SP Archiving.Deadband Value" must be filled.
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | Constraints
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of Controller MV and SP
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | Usage
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as "MV and SP Archiving.Archive Mode"
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | Constraints
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | Description | Deadband value for the SCADA archiving of Controller MV and SP. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | Usage
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as "MV and SP Archiving.Archive Mode"
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | Description | Time filter for the SCADA archiving of Controller MV and SP. Must be positive.
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | Usage
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as "MV and SP Archiving.Archive Mode"
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Modes::Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes
SCADADeviceDataArchiving | Modes::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Modes::Archive Mode | DependentAttributes
SCADADeviceDataArchiving | Modes::Archive Mode | Constraints
SCADADeviceDataArchiving | Output Archiving::Archive Mode | Description | Archive mode of Output. Archive if: Old/New Comparison: value changes Time: value changes after the specified Time Filter Deadband: value < or > specified deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Output Archiving::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Output Archiving::Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Output Archiving::Archive Mode | Constraints
SCADADeviceDataArchiving | Output Archiving::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of Controller Output
SCADADeviceDataArchiving | Output Archiving::Deadband Type | Usage
SCADADeviceDataArchiving | Output Archiving::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as "Output Archiving.Archive Mode"
SCADADeviceDataArchiving | Output Archiving::Deadband Type | Constraints
SCADADeviceDataArchiving | Output Archiving::Deadband Value | Description | Deadband value for the SCADA archiving of Controller Output. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Output Archiving::Deadband Value | Usage
SCADADeviceDataArchiving | Output Archiving::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as "Output Archiving.Archive Mode"
SCADADeviceDataArchiving | Output Archiving::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | Description | Time filter for the SCADA archiving of Controller Output. Must be positive.
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | Usage
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as "Output Archiving.Archive Mode"
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object. Must be positive.
SCADADeviceDataArchiving | Time Filter (s) | Usage
SCADADeviceDataArchiving | Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Totalizer::Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Totalizer::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Totalizer::Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Totalizer::Archive Mode | Constraints
SCADADeviceDataArchiving | Totalizer::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the Totalizer value.
SCADADeviceDataArchiving | Totalizer::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Totalizer::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Totalizer::Deadband Type | Constraints
SCADADeviceDataArchiving | Totalizer::Deadband Value | Description | Deadband value for the SCADA archiving of the Totalizer value. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Totalizer::Deadband Value | Usage
SCADADeviceDataArchiving | Totalizer::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Totalizer::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | Usage
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | Constraints | Must be positive
SCADADeviceFunctionals | Access Control Domain | Description | Define Access Control on the device to an existing SCADA Domain Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | Access Control Domain | Usage | This domain is used to grant access to this specific device. The domain specified for this object will allow access to the object only to registered users on that domain
SCADADeviceFunctionals | Access Control Domain | DependentAttributes
SCADADeviceFunctionals | Access Control Domain | Constraints | Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | Mask Event | Description | If TRUE: the events of the device will be masked in SCADA and not diplayed or archived in the Event List. An 'event' is defined as a bit change in StsReg01 or StsReg02
SCADADeviceFunctionals | Mask Event | Usage
SCADADeviceFunctionals | Mask Event | DependentAttributes
SCADADeviceFunctionals | Mask Event | Constraints
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Description | Define links to other devices (separate device names with commas). Note: it is not necessary to link to master, parents or children because these links are automatically created. Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Usage | Linked devices will be shown in the device right-click menu
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | DependentAttributes | Expert Name or Name. The name of the device(s) specified here *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified here corresponds to "Name".
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Constraints | Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Description | Domain of the device. If empty, the domain will be the name of the application Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Usage | Domain is used to filter the devices in the alarm list or in the device tree overview
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | DependentAttributes
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Description | Nature of the device. If empty, the nature will be the type of the device Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Usage | Nature is used to filter the devices in the alarm list or in the device tree overview
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | DependentAttributes
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | Calibration::Gas Name | Description | Fluid name used to calibrate the device, to be displayed in SCADA.
SCADADeviceGraphics | Calibration::Gas Name | Usage
SCADADeviceGraphics | Calibration::Gas Name | DependentAttributes
SCADADeviceGraphics | Calibration::Gas Name | Constraints
SCADADeviceGraphics | Calibration::Unit | Description | Physical measurement unit selected by the manufacturer of the hardware device during the calibration, to be displayed in SCADA.
SCADADeviceGraphics | Calibration::Unit | Usage | This is the physical unit used by the manufacturer to calibrate the device
SCADADeviceGraphics | Calibration::Unit | DependentAttributes
SCADADeviceGraphics | Calibration::Unit | Constraints
SCADADeviceGraphics | CurveName::CC0 | Description | Fluid name associated with calibration curve 0, to be displayed in SCADA. Cannot be null/empty (there must be at least one fluid).
SCADADeviceGraphics | CurveName::CC0 | Usage
SCADADeviceGraphics | CurveName::CC0 | DependentAttributes
SCADADeviceGraphics | CurveName::CC0 | Constraints | Cannot be null/empty (there must be at least one fluid)
SCADADeviceGraphics | CurveName::CC1 | Description | Fluid name associated with calibration curve 1, to be displayed in SCADA. Can be null/empty.
SCADADeviceGraphics | CurveName::CC1 | Usage
SCADADeviceGraphics | CurveName::CC1 | DependentAttributes
SCADADeviceGraphics | CurveName::CC1 | Constraints | Can be null/empty.
SCADADeviceGraphics | CurveName::CC2 | Description | Fluid name associated with calibration curve 2, to be displayed in SCADA. Can be null/empty.
SCADADeviceGraphics | CurveName::CC2 | Usage
SCADADeviceGraphics | CurveName::CC2 | DependentAttributes
SCADADeviceGraphics | CurveName::CC2 | Constraints | Can be null/empty.
SCADADeviceGraphics | Diagnostic | Description | Define link between the device and an existing diagnostic panel for the device. The panel specified here can be accessed from the device right-click menu item "Diagnostic" as well as from the "Diagnostic" button on the object faceplate.
SCADADeviceGraphics | Diagnostic | Usage | Specify the path of the .pnl file under the "\panel" directory of the PVSS project
SCADADeviceGraphics | Diagnostic | DependentAttributes
SCADADeviceGraphics | Diagnostic | Constraints
SCADADeviceGraphics | Display Name | Description | Short Name displayed in the PCO widget in SCADA. Should be <= 8 characters to be correctly displayed in PCO widget.
SCADADeviceGraphics | Display Name | Usage
SCADADeviceGraphics | Display Name | DependentAttributes
SCADADeviceGraphics | Display Name | Constraints | Should be <= 8 characters to be correctly displayed in PCO widget
SCADADeviceGraphics | Flow::Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Flow::Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Flow::Format | DependentAttributes
SCADADeviceGraphics | Flow::Format | Constraints
SCADADeviceGraphics | Flow::Unit | Description | Physical measurement unit associated with the set point and flow, to be displayed in SCADA.
SCADADeviceGraphics | Flow::Unit | Usage
SCADADeviceGraphics | Flow::Unit | DependentAttributes
SCADADeviceGraphics | Flow::Unit | Constraints
SCADADeviceGraphics | Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Format | DependentAttributes
SCADADeviceGraphics | Format | Constraints
SCADADeviceGraphics | Label Off | Description | SCADA description associated to the State of the object
SCADADeviceGraphics | Label Off | Usage
SCADADeviceGraphics | Label Off | DependentAttributes
SCADADeviceGraphics | Label Off | Constraints
SCADADeviceGraphics | Label On | Description | SCADA description associated to the State of the object
SCADADeviceGraphics | Label On | Usage
SCADADeviceGraphics | Label On | DependentAttributes
SCADADeviceGraphics | Label On | Constraints
SCADADeviceGraphics | Pattern | Description | List of individual messages associated with the value of the object. Strict format: "Nbr=Message,Nbr=Message". The message CAN contain a space.
SCADADeviceGraphics | Pattern | Usage | When not empty, the message corresponding to the value is displayed on the panel.
SCADADeviceGraphics | Pattern | DependentAttributes
SCADADeviceGraphics | Pattern | Constraints | Strict format: "Nbr=Message,Nbr=Message". The message CAN contain a space.
SCADADeviceGraphics | Synoptic | Description | Define link between the device and an existing synoptic where it appears. The synoptic specified here can be accessed from the device right-click menu item "Synoptic".
SCADADeviceGraphics | Synoptic | Usage | Specify the path of the .pnl file under the "\panel" directory of the PVSS project.
SCADADeviceGraphics | Synoptic | DependentAttributes
SCADADeviceGraphics | Synoptic | Constraints
SCADADeviceGraphics | Totalizer::Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Totalizer::Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Totalizer::Format | DependentAttributes
SCADADeviceGraphics | Totalizer::Format | Constraints
SCADADeviceGraphics | Totalizer::Unit | Description | Physical measurement unit associated with the fluid totalizer value, to be displayed in SCADA.
SCADADeviceGraphics | Totalizer::Unit | Usage
SCADADeviceGraphics | Totalizer::Unit | DependentAttributes
SCADADeviceGraphics | Totalizer::Unit | Constraints
SCADADeviceGraphics | Unit | Description | Unit of the device to be displayed in SCADA
SCADADeviceGraphics | Unit | Usage
SCADADeviceGraphics | Unit | DependentAttributes
SCADADeviceGraphics | Unit | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | WWW Link | Description | Define links between the device and existing web pages (or pdf files, or other files which can be opened with IE). The links can be accessed from the device right-click menu item "Info" as well as from the "Info" button on the object faceplate.
SCADADeviceGraphics | WWW Link | Usage | Specify multiple links and corresponding labels by separating them with ¦, e.g.: label1¦link1¦label2¦link2...
SCADADeviceGraphics | WWW Link | DependentAttributes
SCADADeviceGraphics | WWW Link | Constraints
SCADADeviceGraphics | Widget Type | Description | Define the widget type to display in the SCADA device tree overview only. The widget displayed in the process panel will be selected when the user creates the panel.
SCADADeviceGraphics | Widget Type | Usage
SCADADeviceGraphics | Widget Type | DependentAttributes
SCADADeviceGraphics | Widget Type | Constraints
SCADADeviceParameters | F Range Max | Description | Floating value corresponding to the Maximal Range.
SCADADeviceParameters | F Range Max | Usage | When the Widget Type is "Word2AnalogStatus" the word value will be converted at the level of the SCADA into a Float number .
SCADADeviceParameters | F Range Max | DependentAttributes | Widget Type
SCADADeviceParameters | F Range Max | Constraints | Must be present when the Widget Type is "Word2AnalogStatus"
SCADADeviceParameters | F Range Min | Description | Floating value corresponding to the Minimal Range. Must be present when the Widget Type is "Word2AnalogStatus".
SCADADeviceParameters | F Range Min | Usage | When the Widget Type is "Word2AnalogStatus" the word value will be converted at the level of the SCADA into a Float number .
SCADADeviceParameters | F Range Min | DependentAttributes | Widget Type
SCADADeviceParameters | F Range Min | Constraints | Must be present when the Widget Type is "Word2AnalogStatus".
SCADADriverDataSmoothing | Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband)
SCADADriverDataSmoothing | Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Deadband Type | Constraints
SCADADriverDataSmoothing | Deadband Value | Description | Deadband value for the SCADA driver data smoothing Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | Flow::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband) of Flow.
SCADADriverDataSmoothing | Flow::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADriverDataSmoothing | Flow::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Flow::Deadband Type | Constraints | Valid if "Deadband" has been selected as Archive Mode
SCADADriverDataSmoothing | Flow::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Flow. Must be positive and smaller than the deadband specified for the archiving.
SCADADriverDataSmoothing | Flow::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Flow::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Flow::Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing of Controller MV and SP
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | Constraints
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Controller MV and SP. Must be positive and smaller than the deadband specified in "MV and SP Archiving.Deadband Value"
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | Constraints | Must be positive and smaller than the deadband specified in "MV and SP Archiving.Deadband Value"
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband) of Controller Output
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | Constraints
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Controller Output. Must be positive and smaller than the deadband specified in "Output Archiving.Deadband Value"
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | Constraints | Must be positive and smaller than the deadband specified in "Output Archiving.Deadband Value"
SCADADriverDataSmoothing | Totalizer::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband) of Totalizer value.
SCADADriverDataSmoothing | Totalizer::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADriverDataSmoothing | Totalizer::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Totalizer::Deadband Type | Constraints | Valid if "Deadband" has been selected as Archive Mode
SCADADriverDataSmoothing | Totalizer::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Totalizer value. Must be positive and smaller than the deadband specified for the archiving.
SCADADriverDataSmoothing | Totalizer::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Totalizer::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Totalizer::Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving

## DataValidation (hidden)
TRUE | FALSE
DigitalInput | DigitalInputPumpHorizontalLeft | DigitalInputPumpHorizontalRight | DigitalInputPumpVerticalDown | DigitalInputPumpVerticalUp
No | Old/New Comparison
AnalogInput_Small | AnalogInput_SciOrPrecision | AnalogInput_RightSmall | AnalogInput_RightSciOrPrecision | AnalogInput_LeftSmall | AnalogInput_LeftSciOrPrecision | AnalogInput_LeftShort
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
AnalogInput_Small | AnalogInput_SciOrPrecision | AnalogInput_RightSmall | AnalogInput_RightSciOrPrecision | AnalogInput_LeftSmall | AnalogInput_LeftSciOrPrecision | AnalogInput_LeftShort
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Linac | Moore
AnalogInput_Small | AnalogInput_SciOrPrecision | AnalogInput_RightSmall | AnalogInput_RightSciOrPrecision | AnalogInput_LeftSmall | AnalogInput_LeftSciOrPrecision | AnalogInput_LeftShort
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Information | Warning | Alarm | Safety Alarm
DigitalOutput
No | Old/New Comparison
AnalogOutput_Small | AnalogOutput_SciOrPrecision | AnalogOutput_RightSmall | AnalogOutput_RightSciOrPrecision | AnalogOutput_LeftSmall | AnalogOutput_LeftSciOrPrecision
True | False
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
AnalogOutput_Small | AnalogOutput_SciOrPrecision | AnalogOutput_RightSmall | AnalogOutput_RightSciOrPrecision | AnalogOutput_LeftSmall | AnalogOutput_LeftSciOrPrecision
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
DigitalParameter | DigitalParameterKnob | DigitalParameterStat
No | Old/New Comparison
WordParameter | WordParameterStat
No | Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
No | Relative | Absolute | Old/New
AnalogParameter | AnalogParameterStat | AnalogParameterWide
No | Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
No | Relative | Absolute | Old/New
WordStatus | WordStatusWide | WordStatusBit | WordStatusBitBig | WordStatusStep | WordStatusTransition | Word2AnalogStatus | Word2AnalogStatusWide
No | Time | Deadband | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Absolute | Relative
No | Relative | Absolute | Old/New
AnalogStatus | AnalogStatusWide
No | Time | Deadband | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Full/Empty | Full/Half/Empty
TRUE | FALSE
LocalSquare | LocalValveHorizontal | LocalValveVertical | LocalPumpHorizontalLeft | LocalPumpHorizontalRight | LocalPumpVerticalHigh | LocalPumpVerticalLow | LocalDamperVertical | LocalDamperHorizontal | LocalDoubleDamperHorizontal | LocalDoubleDamperVertical | LocalHeaterHorizontal | LocalHeaterVertical | LocalMotor | Local3WayValveHorizontalDownOnLeft | Local3WayValveHorizontalDownOnRight | Local3WayValveHorizontalUpOnLeft | Local3WayValveHorizontalUpOnRight | Local3WayValveVerticalRightOnDown | Local3WayValveVerticalLeftOnUp | Local3WayValveVerticalLeftOnDown | Local3WayValveVerticalRightOnUp
No | Old/New Comparison
On/Open | Off/Close | 2 DO Off | 2 DO On
Full/Empty | Full/Half/Empty
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
OnOffSquare | OnOffMotor | OnOffPumpHorizontalLeft | OnOffPumpHorizontalRight | OnOffPumpVerticalHigh | OnOffPumpVerticalLow | OnOffHeaterHorizontal | OnOffHeaterVertical | OnOffValveHorizontal | OnOffValveVertical | OnOffElectricValveHorizontal | OnOffElectricValveVertical | OnOffFan | OnOffManualValveHorizontal | OnOffManualValveVertical | OnOffDamperHorizontal | OnOffDamperVertical | OnOffDoubleDamperHorizontal | OnOffDoubleDamperVertical | OnOffElecHeaterHorizontal | OnOffElecHeaterVertical | OnOffInvertedValveHorizontal | OnOffInvertedValveVertical | OnOff3WayValveVerticalLeftOnDown | OnOff3WayValveVerticalRightOnUp | OnOff3WayValveHorizontalDownOnLeft | OnOff3WayValveHorizontalDownOnRight | OnOff3WayValveHorizontalUpOnLeft | OnOff3WayValveHorizontalUpOnRight | OnOff3WayValveVerticalLeftOnUp | OnOff3WayValveVerticalRightOnDown | OnOffKnob | OnOffVacPumpPrimaryHorizontal | OnOffVacPumpPrimaryVertical
Off/Close | On/Open Normal Output | On/Open Inverted Output
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
AnalogSquare | AnalogValveHorizontal | AnalogValveVertical | AnalogHeaterHorizontal | AnalogHeaterVertical | AnalogDamperHorizontal | AnalogDamperVertical | AnalogDoubleDamperHorizontal | AnalogDoubleDamperVertical | AnalogElecHeaterHorizontal | AnalogElecHeaterVertical | AnalogFan | AnalogPumpHorizontalLeft | AnalogPumpHorizontalRight | AnalogPumpVerticalUp | AnalogPumpVerticalDown | Analog3WayValveHorizontalDownOnLeft | Analog3WayValveHorizontalDownOnRight | Analog3WayValveHorizontalUpOnLeft | Analog3WayValveHorizontalUpOnRight | Analog3WayValveVerticalLeftOnDown | Analog3WayValveVerticalLeftOnUp | Analog3WayValveVerticalRightOnDown | Analog3WayValveVerticalRightOnUp
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Off/Close | On/Open
Classic | Bipolar
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
AnaDigSquare | AnaDigValveHorizontal | AnaDigValveVertical | AnaDigHeaterHorizontal | AnaDigHeaterVertical
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Off/Close | On/Open
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
AnaDOSquare | AnaDOElecHeaterHorizontal | AnaDOElecHeaterVertical | AnaDOFan | AnaDOHeaterHorizontal | AnaDOHeaterVertical | AnaDOPumpHorizontalLeft | AnaDOPumpHorizontalRight | AnaDOPumpVerticalDown | AnaDOPumpVerticalUp | AnaDOValveHorizontal | AnaDOValveVertical
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
On/Open | Off/Close
TRUE | FALSE
TRUE | FALSE
TRUE | FALSE
TRUE | FALSE
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
MassFlowController
No | Old/New Comparison
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
No | Relative | Absolute | Old/New
2 End Switches + Ref. Switch | 2 End Switches with faked Ref. Switch | 2 Switches plugged into the 1STEP | No End Switches.
Potentiometer | Potentiometer (support) | Encoder
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
SteppingMotor
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Input Scaling | Input/Output Scaling | No Scaling
Controller | ControllerSetPoint | ControllerActiveX
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
No | Relative | Absolute | Old/New
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
PCO | PCOAirHandlingUniHorizontalLeft | PCOAirHandlingUniHorizontalRight | PCOAirHandlingUniVerticalDown | PCOAirHandlingUniVerticalUp | PCOCompressorHorizontalLeft | PCOCompressorHorizontalRight | PCOCompressorVerticalHigh | PCOCompressorVerticalLow | PCOTurbineHorizontalLeft | PCOTurbineHorizontalRight | PCOTurbineVerticalHigh | PCOTurbineVerticalLow
AL | FS | TS | SI | Multiple
DigitalAlarm
No | Old/New Comparison
Information | Warning | Alarm | Safety Alarm
Hardware Interrupt | Cyclic Interrupt
AL | FS | TS | SI | Multiple
AnalogAlarm | AnalogAlarm_Analog | AnalogAlarm_AnalogShort
No | Old/New Comparison
Information | Warning | Alarm | Safety Alarm

## DigitalInput
Name | DigitalInput
Package | CPC
Object Type Family | IOObjectFamily
Description | Digital Input Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  |  | LogicDeviceDefinitions
[6 empty] | FEChannel | [15 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  | Binary State |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Alarm On State | Message | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_NodePCV6126 |  | Distribution rack 61 PA analog valve |  |  | 1 | Mx80_03_PXM_PCV6126_Di | [8 empty] | pxm | DigitalInput |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Di_NodePCV6226 |  | Distribution rack 62 PA analog valve |  |  | 1 | Mx80_03_PXM_PCV6226_Di | [8 empty] | pxm | DigitalInput |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Di_NodeDiFesto1 |  | Distribution festo node 1 |  |  | 1 | Mx80_03_PXM_WAGO_Di | [8 empty] | pxm | DigitalInput |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Di_NodeDiWago1 |  | Distribution profibus slave 1 |  |  | 1 | Mx80_03_PXM_WAGO_Di | [8 empty] | pxm | DigitalInput |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Di_TestLEDS |  | Distribution |  |  | 203 | Mx80_03_PXM_WAGO_Di.Input.DI1 | 0 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalInput |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Xh_TestLEDS |  | Exhaust |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.DI1 | 0 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalInput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Xh_NodeXhWago1 |  | Exhaust profibus wago node unit 1 |  |  | 1 | Mx80_02_PXM_WAGO_Xh | [8 empty] | pxm | DigitalInput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Xh_NodeXMFC5002 |  | Exhaust profibus slave MFC bronkhorst |  |  | 1 | Mx80_02_PXM_XMFC5002 | [8 empty] | pxm | DigitalInput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Xh_ZSH5003 |  | Exhaust selection valve, run end contact |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.DI1 | 2 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalInput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_ZSL5003 |  | Exhaust selection valve, vent end contact |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.DI1 | 1 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalInput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_IS0692_1 |  | GasSystem underground ELMB VC trip for triplet 1 |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI3 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Gs_IS0692_2 |  | GasSystem underground ELMB VC trip for triplet 2 |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI3 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Gs_IS0693_1 |  | GasSystem underground ELMB VD trip for triplet 1 |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI4 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Gs_IS0693_2 |  | GasSystem underground ELMB VD trip for triplet 2 |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI4 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Gs_JS0621 |  | GasSystem underground cavern ELMB PSU fault |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI1 | 5 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_IS0691_1 |  | GasSystem underground ELMB VA trip for triplet 1 |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI2 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Gs_IS0691_2 |  | GasSystem underground ELMB VA trip for triplet 2 |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI2 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Gs_IS0604 |  | GasSystem underground Valves DC circuit breaker status |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI1 | 4 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_YSL0515 |  | GasSystem HW interlock from subdetector via DSS |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Input.DI1 | 7 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Security | TOF_Security |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Gs_IS0504 |  | GasSystem surface Valves DC circuit breaker status |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Input.DI1 | 4 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_IS0503 |  | GasSystem surface Elec. DC circuit breaker status |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Input.DI1 | 3 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_IS0603 |  | GasSystem underground Elec. DC circuit breaker status |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI1 | 3 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_JS0501 |  | GasSystem surface control rack power supply status |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Input.DI1 | 1 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_JS0601 |  | GasSystem service cavern control rack power supply status |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI1 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_NodeGsWago1 |  | GasSystem profibus node 1 Surface(1)/Cavern(2) |  |  | 1 | Mx80_02_PXM_WAGO1_Gs | [8 empty] | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Gs_NodeGsWago2 |  | GasSystem profibus node 2 Surface(1)/Cavern(2) |  |  | 1 | Mx80_03_PXM_WAGO2_Gs | [8 empty] | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Gs_IS0502 |  | GasSystem surface AC circuit breaker status |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Input.DI1 | 2 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_IS0602 |  | GasSystem underground AC circuit breaker status |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.DI1 | 2 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_Gs_TestLEDSCav |  | GasSystem Cavern |  |  | 202 | Mx80_03_PXM_WAGO2_Gs.Input.DI1 |  |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_TestLEDSSur |  | GasSystem Surface |  |  | 202 | Mx80_02_PXM_WAGO1_Gs.Input.DI1 |  |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalInput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_SpareDI1 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI2 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI3 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI4 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI5 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI6 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI7 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI8 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI9 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDI10 |  | Spare DI |  |  | 0 | [10 empty] | DigitalInput |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No
ALITOF_Mx_TestLEDS |  | Mixer |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Input.DI1 | 0 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_ZSH9119 |  | Mixer External hardwired interlock |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Input.DI1 | 1 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Mx_NodeXMFC1109 |  | Mixer L1 HF MFC profibus slave |  |  | 1 | Mx80_02_PXM_XMFC1109 | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Mx_NodeXMFC1209 |  | Mixer L2 HF MFC profibus slave |  |  | 1 | Mx80_02_PXM_XMFC1209 | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Mx_NodeXMFC1309 |  | Mixer L3 HF MFC profibus slave |  |  | 1 | Mx80_02_PXM_XMFC1309 | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Mx_NodeMxWago1 |  | Mixer profibus slave wago 1 |  |  | 1 | Mx80_02_PXM_WAGO_Mx | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Mx_NodeXMFC1106 |  | Mixer L1 LF MFC profibus slave |  |  | 1 | Mx80_02_PXM_XMFC1106 | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Mx_NodeXMFC1206 |  | Mixer L2 LF MFC profibus slave |  |  | 1 | Mx80_02_PXM_XMFC1206 | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Mx_NodeXMFC1306 |  | Mixer L3 LF MFC profibus slave |  |  | 1 | Mx80_02_PXM_XMFC1306 | [8 empty] | pxm | DigitalInput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Pp_TestLEDS |  | test leds |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.DI1 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalInput |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_Pp_P4101DefDis |  | Pump 4101 Circuit breaker tripped (1=Default, 0=OK ) |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.DI1 | 1 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalInput |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Pp_P4201DefDis |  | Pump 4201 Circuit breaker tripped (1=Default, 0=OK ) |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.DI1 | 2 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalInput |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Pp_NodeZC4003 |  | PA analog valve |  |  | 1 | Mx80_03_PXM_ZC4003_Pp | [8 empty] | pxm | DigitalInput |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_Pp_NodePpWago1 |  | wago profibus node 1 accessibility |  |  | 1 | Mx80_03_PXM_WAGO_Pp | [8 empty] | pxm | DigitalInput |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE
ALITOF_P1_TestLEDS |  | Purifier1 |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI2 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | FALSE
ALITOF_P1_ZSH2103 |  | Purifier1 col A input valve open position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI2 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_ZSH2203 |  | Purifier1 col B input valve open position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI3 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_FIS2112 |  | Purifier1 col A regeneration gas flowmeter |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI1 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE
ALITOF_P1_FIS2212 |  | Purifier1 col B regeneration gas flowmeter |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI1 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE
ALITOF_P1_ZSL2103 |  | Purifier1 col A input valve close position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI2 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_ZSL2203 |  | Purifier1 col B input valve close position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI3 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XSS2101 |  | Purifier1 col A interlock read contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI4 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_P1_XSS2201 |  | Purifier1 col B interlock read contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI4 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | FALSE | TRUE
ALITOF_P1_ZSL2107 |  | Purifier1 col A output valve close position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI4 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_ZSL2207 |  | Purifier1 col B output valve close position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI3 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_ZSH2107 |  | Purifier1 col A output valve open position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI4 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_ZSH2207 |  | Purifier1 col B output valve open position contact |  |  | 203 | Mx80_02_PXM_WAGO_P1.Input.DI3 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_NodePuWago1 |  | Purifier1 profibus slave node 1 |  |  | 1 | Mx80_02_PXM_WAGO_P1 | [8 empty] | pxm | DigitalInput |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE | FALSE

## AnalogInput
Name | AnalogInput
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Input Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [5 empty] | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[12 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | Deadband (%) | Filtering Time (s) | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_PT6126 |  | Distribution rack 61 far output PT |  |  | -10 | 10 | 4 | 20 | 0.05 |  | 203 | Mx80_03_PXM_WAGO_Di.Input.AI1 | 1 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.05 |  |  |  | Absolute | 0.01
ALITOF_Di_PT6226 |  | Distribution rack 62 far output PT |  |  | -10 | 10 | 4 | 20 | 0.05 |  | 203 | Mx80_03_PXM_WAGO_Di.Input.AI1 | 3 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.05 |  |  |  | Absolute | 0.01
ALITOF_Di_PT6104 |  | Distribution rack 61 rack chamber PT | PN80:SL03:CH02 |  | -10 | 10 | 4 | 20 | 0.3 |  | 203 | Mx80_03_PXM_WAGO_Di.Input.AI2 | 0 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute | 0.01
ALITOF_Di_PT6204 |  | Distribution rack 62 rack chamber PT | PN80:SL03:CH02 |  | -10 | 10 | 4 | 20 | 0.3 |  | 203 | Mx80_03_PXM_WAGO_Di.Input.AI2 | 2 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute | 0.01
ALITOF_Di_PT6124 |  | Distribution rack 61 near input PT | PN80:SL03:CH01 |  | 0 | 40 | 4 | 20 | 0.3 |  | 203 | Mx80_03_PXM_WAGO_Di.Input.AI1 | 0 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute | 0.1
ALITOF_Di_PT6224 |  | Distribution rack 62 near input PT | PN80:SL03:CH01 |  | 0 | 40 | 4 | 20 | 0.3 |  | 203 | Mx80_03_PXM_WAGO_Di.Input.AI1 | 2 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute | 0.1
ALITOF_Xh_PT5005 |  | Exhaust buffer pressure transmitter |  |  | 0 | 5 | 4 | 20 | 0.05 |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.AI1 | 0 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm455 | bar | ##.### | AnalogInput_Small | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.025 |  |  |  | Absolute | 0.003
ALITOF_Xh_PDT5030 |  | Exhaust filter differential pressure transmitter |  |  | 0.0 | 200.0 | 4 | 20 | 0.05 |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.AI1 | 3 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm455 | bar | ##.### | AnalogInput_Small | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800 | Absolute | 0.07 |  |  |  | Absolute | 0.05
ALITOF_Xh_FIT5010 |  | Exhaust circulation flowmeter |  |  | 0 | 2 | 4 | 20 | 1.0 |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.AI1 | 2 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm455 | Nm3/h | #.## | AnalogInput_Small | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.05 |  |  |  | Absolute | 0.02
ALITOF_Xh_PT5011 |  | Exhaust circulation pressure transmitter |  |  | 0 | 5 | 4 | 20 | 0.2 |  | 203 | Mx80_02_PXM_WAGO_Xh.Input.AI1 | 1 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.02 |  |  |  | Absolute | 0.01
ALITOF_Gs_IT24VDCSur |  | GasSystem Surface 24VDC current consumption |  |  | 0.0 | 40.0 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO1_Gs.Input.AI1 | 0 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm455 | A | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Gs_IT24VDCCav |  | GasSystem Underground 24VDC current consumption |  |  | 0.0 | 40.0 | 4 | 20 | 0.5 |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.AI1 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm455 | A | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Gs_IT18VDCCav |  | GasSystem Underground 18VDC current consumption |  |  | 0.0 | 40.0 | 4 | 20 | 0.5 |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.AI1 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm455 | A | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Gs_18VDCCav |  | GasSystem Underground 18VDC voltage |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 203 | Mx80_03_PXM_WAGO2_Gs.Input.AI1 | 2 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm455 | V | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Gs_SpareAI1 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI2 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI3 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI4 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI5 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI6 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI7 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI8 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI9 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Gs_SpareAI10 |  | GasSystem Spare AI |  |  | 0.0 | 25.0 | 4 | 20 | 0.5 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.03 |  |  |  | No | 0.1
ALITOF_Mx_PT1103 |  | Mixer L1 input PT |  |  | -1 | 3 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO_Mx.Input.AI1 | 0 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.04 |  |  |  | Absolute | 0.04
ALITOF_Mx_PT1203 |  | Mixer L2 input PT |  |  | -1 | 3 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO_Mx.Input.AI1 | 1 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.04 |  |  |  | Absolute | 0.04
ALITOF_Mx_PT1303 |  | Mixer L3 input PT |  |  | -1 | 3 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO_Mx.Input.AI1 | 2 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.04 |  |  |  | Absolute | 0.04
ALITOF_Mx_PT1009 |  | Mixer output PT |  |  | -1 | 3 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO_Mx.Input.AI1 | 3 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.04 |  |  |  | Absolute | 0.02
ALITOF_Pp_TE4101_1 |  | pump device 1 upper temperature sensor |  |  | -200 | 850 | -2000 | 8500 | 0.05 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI3 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm460 | C | #.# | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 3600.0 | Absolute | 0.5 |  |  |  | Absolute | 0.2
ALITOF_Pp_TE4201_1 |  | pump device 2 upper temperature sensor |  |  | -200 | 850 | -2000 | 8500 | 0.05 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI3 | 2 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm460 | C | ##.# | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 3600.0 | Absolute | 0.5 |  |  |  | Absolute | 0.2
ALITOF_Pp_PT4101_1 |  | pump device 1 first membrane pressure |  |  | 0 | 5 | 4 | 20 | 1.0 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI1 | 2 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute
ALITOF_Pp_PT4201_1 |  | pump device 2 first membrane pressure |  |  | 0.0 | 5 | 4 | 20 | 1.0 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI2 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm455 | bar | ##.## | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute
ALITOF_Pp_PT4006 |  | output pressure control transmitter |  |  | 0 | 5 | 4 | 20 | 1.0 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI1 | 1 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm455 | bar | #.## | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.05 |  |  |  | Absolute | 0.05
ALITOF_Pp_PT4004 |  | input pressure control transmitter |  |  | -100 | 100 | 4 | 20 | 0.02 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI1 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm455 | mbar | #.## | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.04
ALITOF_Pp_PDT4020 |  | outlet filter differential PT |  |  | -50 | 20.0 | 4 | 20 | 1.0 |  | 203 | Mx80_03_PXM_WAGO_Pp.Input.AI2 | 2 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm455 | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800 | Absolute | 1.4 |  |  |  | Absolute | 1.0
ALITOF_P1_TE2101_3 |  | Purifier1 col A internal middle temperature |  |  | -200 | 850 | -2000 | 8500 | 0.1 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI3 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm460 | C | #.## | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 1800.0 | Absolute | 3.0 |  |  |  | Absolute | 1.0
ALITOF_P1_TE2201_3 |  | Purifier1 col B internal middle temperature |  |  | -200 | 850 | -2000 | 8500 | 0.1 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI3 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm460 | C | #.## | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 1800.0 | Absolute | 3.0 |  |  |  | Absolute | 1.0
ALITOF_P1_PT2108 |  | Purifier1 col A output pressure |  |  | -1 | 5 | 4 | 20 | 1.0 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI1 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm455 | bar | #.### | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 60.0 | Absolute | 0.005 |  |  |  | Absolute | 0.005
ALITOF_P1_PT2208 |  | Purifier1 col B output pressure |  |  | -1 | 5 | 4 | 20 | 1.0 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI1 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm455 | bar | #.### | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 60.0 | Absolute | 0.005 |  |  |  | Absolute | 0.005
ALITOF_P1_TE2101_2 |  | Purifier1 col A external temperature |  |  | -200 | 850 | -2000 | 8500 | 0.1 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI2 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm460 | C | #.## | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 1800.0 | Absolute | 3.0 |  |  |  | Absolute | 1.0
ALITOF_P1_TE2201_2 |  | Purifier1 col B external temperature |  |  | -200 | 850 | -2000 | 8500 | 0.1 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI2 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm460 | C | #.## | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 1800.0 | Absolute | 3.0 |  |  |  | Absolute | 1.0
ALITOF_P1_FIT2109 |  | Purifier1 col A input flowmeter |  |  | 0 | 2 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI1 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm455 | Nm3/h | #.## | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.05 |  |  |  | Absolute | 0.01
ALITOF_P1_FIT2209 |  | Purifier1 col B input flowmeter |  |  | 0 | 2 | 4 | 20 | 0.5 |  | 203 | Mx80_02_PXM_WAGO_P1.Input.AI1 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm455 | Nm3/h | #.## | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.05 |  |  |  | Absolute | 0.01

## AnalogInputReal
Name | AnalogInputReal
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Input Real Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [5 empty] | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[12 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | Deadband (%) | Filtering Time (s) | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_ZC6126F |  | Distribution rack 61 pressure regulation valve feedback |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 204 | Mx80_03_PXM_PCV6126_Di |  |  |  |  | ALITOF_Di_NodePCV6126 |  |  |  | pxmSipart | % | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Relative | 0.1
ALITOF_Di_ZC6226F |  | Distribution rack 62 pressure regulation valve feedback |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 204 | Mx80_03_PXM_PCV6226_Di |  |  |  |  | ALITOF_Di_NodePCV6226 |  |  |  | pxmSipart | % | #.## | AnalogInput_Small | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Relative | 0.1
ALITOF_Di_PumpMvRack61 |  | Distribution rack 61 Pump Module Measured Value for CN4003 |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 0 | [5 empty] | ALITOF_Di_NodeDiWago2 |  |  |  |  | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Relative | 1.0
ALITOF_Di_PumpMvRack62 |  | Distribution rack 62 Pump Module Measured Value for CN4003 |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 0 | [5 empty] | ALITOF_Di_NodeDiWago2 |  |  |  |  | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Relative | 1.0
ALITOF_Di_CN6126MV |  | Distribution rack 61 pressure regulation measured value |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 0 | [5 empty] | ALITOF_Di_NodeDiWago2 |  |  |  |  | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Relative | 1.0
ALITOF_Di_CN6226MV |  | Distribution rack 62 pressure regulation measured value |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 0 | [5 empty] | ALITOF_Di_NodeDiWago2 |  |  |  |  | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Relative | 1.0
ALITOF_Gs_PT0201 |  | GasSystem service cavern atmospheric pressure |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 101 | %MW15004 | [9 empty] | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 10.0 | Absolute | 0.2 |  |  |  | Absolute | 0.01
ALITOF_Gs_PT0101 |  | GasSystem surface atmospheric pressure |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 101 | %MW15002 | [9 empty] | mbar | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 10.0 | Absolute | 0.2 |  |  |  | Absolute | 0.01
ALITOF_Gs_SpareAIR1 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR2 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR3 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR4 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR5 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR6 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR7 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR8 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR9 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Gs_SpareAIR10 |  | GasSystem Spare AIR |  |  | 0.0 | 2000.0 | 0.0 | 2000.0 | 0.01 |  | 0 | [11 empty] | ##.# | AnalogInput_Small | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.2 |  |  |  | No | 0.01
ALITOF_Pp_ZC4003F |  | pressure control valve position |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 0.1 |  | 204 | Mx80_03_PXM_ZC4003_Pp |  |  |  |  | ALITOF_Pp_NodeZC4003 |  |  |  | pxmSipart | % | #.## | AnalogInput_Small | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 0.1
ALITOF_P1_CNTZ2101MV |  | Purifier1 CNTZ2101 Measured value |  |  | -400.0 | 1700.0 | -400.0 | 1700.0 | 0.1 |  | 0 | [10 empty] | C | ##.# | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 1800 | Absolute | 4.2 |  |  |  | Absolute | 0.2
ALITOF_P1_CNTZ2201MV |  | Purifier1 CNTZ2201 Measured value |  |  | -400.0 | 1700.0 | -400.0 | 1700.0 | 0.1 |  | 0 | [10 empty] | C | ##.# | AnalogInput_Small | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temp |  | Deadband AND Time | 1800 | Absolute | 4.2 |  |  |  | Absolute | 0.2

## Encoder
Name | Encoder
Package | CPC
Object Type Family | IOObjectFamily
Description | Encoder Device
Version | 1.0
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [5 empty] | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [8 empty] | LogicDeviceDefinitions
[12 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | Deadband (%) | Encoder Type | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Level | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## DigitalOutput
Name | DigitalOutput
Package | CPC
Object Type Family | IOObjectFamily
Description | Digital Output Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  |  | LogicDeviceDefinitions
[6 empty] | FEChannel | [15 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  | Binary State |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Alarm On State | Message | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_YY6171 |  | Distribution rack 61 safety backup valve DO | PN80:SL05:CH00 |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 2 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6271 |  | Distribution rack 62 safety backup valve DO | PN80:SL05:CH00 |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 6 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_XLED60991 |  | Distribution Run state LED DO | PN50:SL07:CH00 |  | 203 | Mx80_03_PXM_WAGO_Di.Output.DO1 | 0 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_XLED60992 |  | Distribution Not Ready state LED DO | PN50:SL09:CH02 |  | 203 | Mx80_03_PXM_WAGO_Di.Output.DO1 | 1 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_XLED60993 |  | Distribution Com. purge state LED DO | PN50:SL07:CH01 |  | 203 | Mx80_03_PXM_WAGO_Di.Output.DO1 | 2 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_XLED60994 |  | Distribution Stop state LED DO | PN50:SL07:CH02 |  | 203 | Mx80_03_PXM_WAGO_Di.Output.DO1 | 3 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_XLED60995 |  | Distribution Proc. ctl alarm LED DO | PN50:SL07:CH03 |  | 203 | Mx80_03_PXM_WAGO_Di.Output.DO1 | 4 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_XLED60996 |  | Distribution Interlock LED DO | PN50:SL07:CH04 |  | 203 | Mx80_03_PXM_WAGO_Di.Output.DO1 | 5 |  |  |  | ALITOF_Di_NodeDiWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6123 |  | Distribution rack 61 input valve DO | PN50:SL13:CH02 |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 0 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6223 |  | Distribution rack 62 input valve DO | PN50:SL13:CH02 |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 4 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6127 |  | Distribution rack 61 output valve DO |  |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 1 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6227 |  | Distribution rack 62 output valve DO |  |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 5 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6172 |  | Distribution rack 61 output sel. valve DO | PN80:SL05:CH01 |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 3 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Di_YY6272 |  | Distribution rack 62 output sel. valve DO | PN80:SL05:CH01 |  | 203 | Mx80_03_PXM_FESTO_Di.Output.DO1 | 7 |  |  |  | ALITOF_Di_NodeDiFesto1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_XLED5099_3 |  | Exhaust stop state LED |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO1 | 4 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_XLED5099_4 |  | Exhaust process control alarms LED |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO1 | 5 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_XLED5099_5 |  | Exhaust interlocks LED |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO1 | 6 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_XLED5099_2 |  | Exhaust venting state LED |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO1 | 1 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_YYH5003 |  | Exhaust selection valve, open command |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO2 | 0 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_YYL5003 |  | Exhaust selection valve, close command |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO2 | 1 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Xh_XLED5099_1 |  | Exhaust run state LED |  |  | 203 | Mx80_02_PXM_WAGO_Xh.Output.DO1 | 0 |  |  |  | ALITOF_Xh_NodeXhWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0507 |  | GasSystem surface 24v valves MCB reset cmd |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO3 | 5 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0506 |  | GasSystem surface 24v elec MCB reset cmd |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO3 | 4 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_20 |  | GasSystem surface Gas System ready for physics status (DSS) LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO3 | 3 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_13 |  | GasSystem underground PSU fault LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 6 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_15 |  | GasSystem surface WebMas running LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO2 | 0 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_12 |  | GasSystem surface control rack PLC ioSim LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO2 | 1 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_12 |  | GasSystem underground control rack PLC ioSim LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_13 |  | GasSystem surface PSU fault LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO2 | 6 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_18 |  | GasSystem surface 24v MCB trip LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO3 | 1 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_17 |  | GasSystem surface AC MCB trip LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO3 | 0 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_17 |  | GasSystem underground AC MCB trip LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO3 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_14 |  | GasSystem underground ELMB PSU fault LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 7 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0610 |  | GasSystem underground ELMB VD MCB reset cmd |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO5 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_19 |  | GasSystem underground ELMB MCB trip LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO3 | 2 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_20 |  | GasSystem underground Gas System ready for physics status (DSS) LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO3 | 3 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_15 |  | GasSystem underground WebMas running LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0609 |  | GasSystem underground ELMB VC MCB reset cmd |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO5 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_18 |  | GasSystem underground 24v MCB trip LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO3 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0606 |  | GasSystem underground 24v elec MCB reset cmd |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO3 | 4 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0608 |  | GasSystem underground ELMB VA MCB reset cmd |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XRES0607 |  | GasSystem underground 24v valves MCB reset cmd |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO3 | 5 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_7 |  | GasSystem surface control rack interlocks LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 6 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_6 |  | GasSystem surface control rack process alarms LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 5 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_8 |  | GasSystem surface control rack PLC running LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 7 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_11 |  | GasSystem surface control rack PLC ioErr LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO2 | 2 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_9 |  | GasSystem surface control rack PLC Profibus OK LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO2 | 3 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_5 |  | GasSystem surface control rack STOP state LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 4 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_1 |  | GasSystem surface control rack RUN state LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 0 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_GSY0505 |  | GasSystem gas system status for sub-detector (DSS) |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO4 | 0 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_2 |  | GasSystem surface control rack FILL state LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 1 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_4 |  | GasSystem surface control rack RECUPERATION state LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 3 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_3 |  | GasSystem surface control rack PURGE state LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO1 | 2 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0599_10 |  | GasSystem surface control rack PLC canbus OK LED |  |  | 203 | Mx80_02_PXM_WAGO1_Gs.Output.DO2 | 4 |  |  |  | ALITOF_Gs_NodeGsWago1 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_8 |  | GasSystem underground control rack PLC running LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 7 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_7 |  | GasSystem underground control rack interlocks state LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 6 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_9 |  | GasSystem underground control rack PLC profibus OK LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 3 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_11 |  | GasSystem underground control rack PLC ioErr LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 2 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_10 |  | GasSystem underground control rack PLC canbus OK LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO2 | 4 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_6 |  | GasSystem underground control rack process alarms state LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 5 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_2 |  | GasSystem underground control rack FILL state LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 1 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_1 |  | GasSystem underground control rack RUN state LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 0 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_3 |  | GasSystem underground control rack PURGEstate LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 2 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_5 |  | GasSystem underground control rack STOP state LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 4 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_XLED0699_4 |  | GasSystem underground control rack RECUPERATIONstate LED |  |  | 203 | Mx80_03_PXM_WAGO2_Gs.Output.DO1 | 3 |  |  |  | ALITOF_Gs_NodeGsWago2 |  |  |  | pxm | DigitalOutput |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO1 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO2 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO3 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO4 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO5 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO6 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO7 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO8 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO9 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Gs_SpareDO10 |  | GasSystem Spare DO |  |  | 0 | [9 empty] | pxm | DigitalOutput |  |  |  | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_1 |  | Mixer Run LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 2 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_2 |  | Mixer Fill LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 0 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_3 |  | Mixer Purge LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 1 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_4 |  | Mixer Direct Mode LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 3 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_5 |  | Mixer Stop LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 4 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_6 |  | Mixer Process Alarm LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 5 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_XLED1099_7 |  | Mixer Interlock LED |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO1 | 6 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1105 |  | Mixer L1 LF electrovanne |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO2 | 0 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1205 |  | Mixer L2 LF electrovanne |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO2 | 2 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1305 |  | Mixer L3 LF electrovanne |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO3 | 3 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1108 |  | Mixer L1 HF electrovanne |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO2 | 1 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1208 |  | Mixer L2 HF electrovanne |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO2 | 3 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1308 |  | Mixer L3 HF electrovanne |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO4 | 0 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1004 |  | Mixer cst. flow sel. valve DO |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO3 | 0 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1006 |  | Mixer fill pres. reg. sel. valve DO |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO3 | 1 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Mx_YV1008 |  | Mixer bypass sel. valve DO |  |  | 203 | Mx80_02_PXM_WAGO_Mx.Output.DO3 | 2 |  |  |  | ALITOF_Mx_NodeMxWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_YV4002 |  | bypass secutiry valve associated DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO2 | 1 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4099_6 |  | interlock LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 6 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_YC4101 |  | on/off pump 1 DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO2 | 3 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_YC4201 |  | on/off pump 2 DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO3 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_YY4040 |  | output valve associated DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO2 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4099_5 |  | process control alarms LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 5 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4101 |  | pump device 1 status LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 2 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4201 |  | pump device 2 status LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 3 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4099_1 |  | run state LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 0 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4099_3 |  | starting state LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 1 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_Pp_XLED4099_4 |  | stop state LED DO |  |  | 203 | Mx80_03_PXM_WAGO_Pp.Output.DO1 | 4 |  |  |  | ALITOF_Pp_NodePpWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_1 |  | Purifier1 col A run sequence state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_1 |  | Purifier1 col B run sequence state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_2 |  | Purifier1 col A regeneration sequence state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_2 |  | Purifier1 col B regeneration sequence state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_3 |  | Purifier1 col A cool down state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_3 |  | Purifier1 col B cool down state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_4 |  | Purifier1 col A stand by state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_4 |  | Purifier1 col B stand by state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_5 |  | Purifier1 col A purge state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 4 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_5 |  | Purifier1 col B purge state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 4 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_6 |  | Purifier1 col A stop state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 5 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_6 |  | Purifier1 col B stop state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 5 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_8 |  | Purifier1 col A process control alarms led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 6 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_8 |  | Purifier1 col B process control alarms led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 6 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2199_9 |  | Purifier1 col A interlock led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO2 | 7 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2299_9 |  | Purifier1 col B interlock led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO3 | 7 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_1 |  | Purifier1 run state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_2 |  | Purifier1 single column A state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_3 |  | Purifier1 single column B state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_4 |  | Purifier1 double column state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_5 |  | Purifier1 free run state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 4 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_6 |  | Purifier1 stop state led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 5 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_8 |  | Purifier1 process control alarms led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 6 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_XLED2099_9 |  | Purifier1 process control interlock led DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO1 | 7 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | led |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YIC2005 |  | Purifier1 extraction pump DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO5 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2103 |  | Purifier1 col A input valve |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO6 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2203 |  | Purifier1 col B input valve |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO7 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2104 |  | Purifier1 col A purge/regeneration output valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO8 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2204 |  | Purifier1 col B purge/regeneration output valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO9 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2105 |  | Purifier1 col A prepare for run/purge valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO8 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2205 |  | Purifier1 col B prepare for run/purge valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO9 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2106 |  | Purifier1 col A purge/regeneration input valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO8 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2206 |  | Purifier1 col B purge/regeneration input valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO9 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2107 |  | Purifier1 col A output valve |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO6 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2207 |  | Purifier1 col B output valve |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO7 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2110 |  | Purifier1 col A purge valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO6 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2210 |  | Purifier1 col B purge valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO7 | 2 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2111 |  | Purifier1 col A regeneration valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO6 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2211 |  | Purifier1 col B regeneration valve DO |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO7 | 3 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2001_1 |  | Purifier1 bypass valve |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO5 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE
ALITOF_P1_YY2001_2 |  | Purifier1 selection valve |  |  | 203 | Mx80_02_PXM_WAGO_P1.Output.DO5 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm | DigitalOutput | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | TRUE

## AnalogOutput
Name | AnalogOutput
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Output Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters |  |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[10 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Gs_SpareAO1 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO2 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO3 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO4 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO5 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO6 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO7 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO8 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO9 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_Gs_SpareAO10 |  | Spare AO |  |  | 0 | 2.0 | 0 | 2000 | 0 | [11 empty] | #.## | AnalogOutput_Small |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  | Absolute |  |  |  |  | No
ALITOF_P1_TZY2101 |  | Purifier1 col A heater AO |  |  | 0.0 | 100.0 | 7 | 32767 | 203 | Mx80_02_PXM_WAGO_P1.Output.AO1 | 0 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm550 | % | #.## | AnalogOutput_Small |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | heater |  | No | [6 empty] | Absolute | 1.0
ALITOF_P1_TZY2201 |  | Purifier1 col B heater AO |  |  | 0.0 | 100.0 | 7 | 32767 | 203 | Mx80_02_PXM_WAGO_P1.Output.AO1 | 1 |  |  |  | ALITOF_P1_NodePuWago1 |  |  |  | pxm550 | % | #.## | AnalogOutput_Small |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | heater |  | No | [6 empty] | Absolute | 1.0

## AnalogOutputReal
Name | AnalogOutputReal
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Output Real Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters |  |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[10 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_ZC6126 |  | Distribution rack 61 pressure regulation valve |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 204 | Mx80_03_PXM_PCV6126_Di |  |  |  |  | ALITOF_Di_NodePCV6126 |  |  |  | pxmsipart | % | #.## | AnalogOutput_Small | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 1.5
ALITOF_Di_ZC6226 |  | Distribution rack 62 pressure regulation valve |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 204 | Mx80_03_PXM_PCV6226_Di |  |  |  |  | ALITOF_Di_NodePCV6226 |  |  |  | pxmsipart | % | #.## | AnalogOutput_Small | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 1.5
ALITOF_Pp_ZC4003 |  | pressure control valve setpoint |  |  | 0.0 | 100.0 | 0.0 | 100.0 | 204 | Mx80_03_PXM_ZC4003_Pp |  |  |  |  | ALITOF_Pp_NodeZC4003 |  |  |  | pxmsipart | % | #.## | AnalogOutput_Small |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 0.5

## DigitalParameter
Name | DigitalParameter
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Digital Parameter Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving
SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Default Value | Widget Type | Label On | Label Off | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive
ALITOF_Di_SignFlow |  | (RunNotReady) significant flow condition relevant for rack operation (1=Relevant, 0=NOT relevant) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_AbsPreRegDP |  | Absolute pressure selection for regulation (1=Absolute, 0=Relative) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_CriticGasDP |  | Critical gas loss (1=Critical, 0=Not critical) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_Rack61Sel |  | Rack 61 selection (1=relevant for global operation, 0=not relevant) |  | TRUE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_Rack62Sel |  | Rack 62 selection (1=relevant for global operation, 0=not relevant) |  | TRUE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_PT6104_Sel |  | Rack 61 Pressure sensor selection for regulation (0=PT6104 /2, 1= PT6126) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_PT6204_Sel |  | Rack 62 Pressure sensor selection for regulation (0=PT6204 /2, 1= PT6226) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_PT61041FT1Sel |  | PT6104/1 in IO Error or significant deviation between PT6126 and PT6104/1 detected Selection (1=Sel) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_PT62041FT1Sel |  | PT6204/1 in IO Error or significant deviation between PT6226 and PT6204/1 detected Selection (1=Sel) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_PT61042FT1Sel |  | PT6104/2 in IO Error or significant deviation between PT6126 and PT6104/2 detected Selection (1=Sel) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Di_PT62042FT1Sel |  | PT6204/2 in IO Error or significant deviation between PT6226 and PT6204/2 detected Selection (1=Sel) |  | FALSE | DigitalParameter |  |  |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Xh_BuffPrRegFlag |  | Activation of the buffer pressure regulation (1=regulation activated /0=not activated) |  | TRUE | DigitalParameter |  |  |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_DiDSSRelev |  | Dsitribution Module is relevant for DSS (ready for physics) signal |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_DiGlbRelev |  | Distribution Module is relevant for global operation |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_MxDSSRelev |  | Mixer Module is relvant for DSS (ready for physics) signal |  | FALSE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_MxGlbRelev |  | Mixer Module is relevant for global operation |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_OpMxReqFlag |  | Mixer not in compliant state alarm enabling (1:enabled, 0:ignored) |  | FALSE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_P1DSSRelev |  | Purifier1 Module is relevant for DSS (ready for physics) signal |  | FALSE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_P1GlbRelev |  | Purifier1 Module is relevant for global operation |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_P1InRecup |  | Purifier 1 module state selection for Gas System Recuperating (1: Run, 0: Stop) |  | FALSE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_P1InRun |  | Purifier 1 module state selection for Gas System Run (1: Run, 0: Stop) |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_PpDSSRelev |  | Pump Module is relevant for DSS (ready for physics) signal |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_PpGlbRelev |  | Pump Module is relevant for global operation |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_XhDSSRelev |  | Exhaust Module is relevant for DSS (ready for physics) signal |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_XhGlbRelev |  | Exhaust Module is relevant for global operation |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_XhInFill |  | Exhaust module state selection for Gas System Fill (1: Run, 0: Venting) |  | TRUE | DigitalParameter |  |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Gs_SpareDP1 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP2 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP3 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP4 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP5 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP6 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP7 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP8 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP9 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Gs_SpareDP10 |  | Spare DPAR |  | FALSE | DigitalParameter | [6 empty] | TOF_Details | TOF_Details |  |  | No
ALITOF_Mx_FillComp |  | Activation of Fill auto completion (1=transition enabled) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L1DirectLF |  | (Direct) Line 1 MFC selection (1=XMFC1106,0=XMFC1109) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L2DirectLF |  | (Direct) Line 2 MFC selection (1=XMFC1206,0=XMFC1209) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L3DirectLF |  | (Direct) Line 3 MFC selection (1=XMFC1306,0=XMFC1309) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L1FillLF |  | (Fill) Line 1 MFC selection (1=XMFC1106,0=XMFC1109) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L2FillLF |  | (Fill) Line 2 MFC selection (1=XMFC1206,0=XMFC1209) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L3FillLF |  | (Fill) Line 3 MFC selection (1=XMFC1306,0=XMFC1309) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L1PurgeLF |  | (Purge) Line 1 MFC selection (1=XMFC1106,0=XMFC1109) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L2PurgeLF |  | (Purge) Line 2 MFC selection (1=XMFC1206,0=XMFC1209) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L3PurgeLF |  | (Purge) Line 3 MFC selection (1=XMFC1306,0=XMFC1309) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L1RunLF |  | (Run) Line 1 MFC selection (1=XMFC1106,0=XMFC1109) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L2RunLF |  | (Run) Line 2 MFC selection (1=XMFC1206,0=XMFC1209) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_L3RunLF |  | (Run) Line 3 MFC selection (1=XMFC1306,0=XMFC1309) |  | TRUE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Mx_PurgeComp |  | Activation of Purge auto completion (1=transition enabled) |  | FALSE | DigitalParameter |  |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Pp_Pump1Selected |  | PUMP4101 selection (1=selected, 0=not selected) |  | TRUE | DigitalParameter |  |  |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_Pp_Pump2Selected |  | PUMP4201 selection (1=selected, 0=not selected) |  | FALSE | DigitalParameter |  |  |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_P1_CAMntStartInt |  | Column A cannot be used due to maintenance activity (1=Disabled, 0=Enabled) |  | FALSE | DigitalParameter |  |  |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_P1_CBMntStartInt |  | Column B cannot be used due to maintenance activity (1=Disabled, 0=Enabled) |  | FALSE | DigitalParameter |  |  |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_P1_PumpInPforRun |  | (Prepare for run) Pump selection (1=Selected, 0=Not selected) |  | TRUE | DigitalParameter |  |  |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_P1_PumpInRegnSeq |  | (Regeneration sequence) Pump selection(1=Selected, 0=Not selected) |  | TRUE | DigitalParameter |  |  |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison
ALITOF_P1_SkipPrep |  | Skip Preparation for Run after restart (1=Selected, 0=Not Selected) |  | FALSE | DigitalParameter |  |  |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison

## WordParameter
Name | WordParameter
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Word Parameter Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [6 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  |  | SCADADriverDataSmoothing
[8 empty] | FEChannel | [18 empty] | SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Range Min | Range Max | Default Value | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Pattern | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value
ALITOF_Di_ChamPRegWP |  | Pressure sensor selection for racks pressure regulator |  | 0 | 3 | 0 | [12 empty] | ##### | WordParameter | 1=PTxx04 Chamber pressure, 2 = PTxx05 Dummy Chamber pressure, 3 = Rack output pressure |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_FCRck61Cmd1WP |  | Rack 61 flow cell selection (Bit pattern: Edit from panel!) |  | 0 | 65535 | 65535 | [12 empty] | ##### | WordParameter |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Di_FCRck61Cmd2WP |  | Rack 61 flow cell selection (Bit pattern: Edit from panel!) |  | 0 | 65535 | 3 | [12 empty] | ##### | WordParameter |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Di_FCRck62Cmd1WP |  | Rack 62 flow cell selection (Bit pattern: Edit from panel!) |  | 0 | 65535 | 65535 | [12 empty] | ##### | WordParameter |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Di_FCRck62Cmd2WP |  | Rack 62 flow cell selection (Bit pattern: Edit from panel!) |  | 0 | 65535 | 3 | [12 empty] | ##### | WordParameter |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Xh_MFCCurCurve |  | XMFC5002 - Calibration curve selection |  | 0 | 2 | 0 | [11 empty] | - | ##### | WordParameter |  |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Gs_SpareWP1 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP2 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP3 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP4 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP5 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP6 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP7 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP8 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP9 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareWP10 |  | Spare WP |  | 0 | 100 | 0 | [12 empty] | ##### | WordParameter | [5 empty] | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Mx_L1HighFlCur |  | XMFC1109 - (Fill/Run/Direct) Line 1 calibration curve for high flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L2HighFlCur |  | XMFC1209 - (Fill/Run/Direct) Line 2 calibration curve for high flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L3HighFlCur |  | XMFC1309 - (Fill/Run/Direct) Line 3 calibration curve for high flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L1LowFlCur |  | XMFC1106 - (Fill/Run/Direct) Line 1 calibration curve for low flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L2LowFlCur |  | XMFC1206 - (Fill/Run/Direct) Line 2 calibration curve for low flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L3LowFlCur |  | XMFC1306 - (Fill/Run/Direct) Line 3 calibration curve for low flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L1HFPurCur |  | XMFC1109 - (Purge) Line 1 calibration curve for high flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No
ALITOF_Mx_L1LFPurCur |  | XMFC1106 - (Purge) Line 1 calibration curve for low flow |  | 0 | 1 | 0 | [12 empty] | ##### | WordParameter |  |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No

## AnalogParameter
Name | AnalogParameter
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Analog Parameter Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  |  | SCADADriverDataSmoothing
SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Range Min | Range Max | Default Value | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value
ALITOF_Di_61PRegAlH |  | Rack 61 pressure regulation H (-L) alarm threshold |  | -15.0 | 15.0 | 2.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_62PRegAlH |  | Rack 62 pressure regulation H (-L) alarm threshold |  | -15.0 | 15.0 | 2.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_61PRegAlHH |  | Rack 61 pressure regulation HH (-LL) alarm threshold |  | -15.0 | 15.0 | 10.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_62PRegAlHH |  | Rack 62 pressure regulation HH (-LL) alarm threshold |  | -15.0 | 15.0 | 10.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_AlmDATOTP |  | Racks state related alarms delay |  | 0.0 | 300.0 | 5.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_AtmPresAATOTP |  | PT0201 - Atmospheric pressure alarm delay |  | 0.0 | 50.0 | 20.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_AtmPressAAHH |  | PT0201 - Atmospheric pressure HH alarm threshold |  | 0.0 | 10000.0 | 1100.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_AtmPressAALL |  | PT0201 - Atmospheric pressure LL alarm threshold |  | 0.0 | 10000.0 | 900.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_AtmPrSeDATOTP |  | PT0201 - Atmospheric pressure transmitter alarm delay |  | 0.0 | 5.0 | 1.0 | h | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_BackUpAlTOTP |  | PT5509, PSL5508 - Backup low pressure alarms delay |  | 0.0 | 300.0 | 30.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_ChamPRegAAH |  | PTxx04 - chamber pressure H alarm threshold |  | -2.0 | 2.0 | 2.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_ChamPRegAAHH |  | PTxx04 - chamber pressure HH alarm threshold |  | -3.0 | 2.5 | 2.5 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_ChamPRegAAL |  | PTxx04 - chamber pressure L alarm threshold |  | -2.0 | 0.0 | -1.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_ChamPRegAALL |  | PTxx04 - chamber pressure LL alarm threshold |  | -3.0 | 0.0 | -2.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan1Vol61 |  | Rack 61 channel 1 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan2Vol61 |  | Rack 61 channel 2 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan3Vol61 |  | Rack 61 channel 3 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan4Vol61 |  | Rack 61 channel 4 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan5Vol61 |  | Rack 61 channel 5 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan6Vol61 |  | Rack 61 channel 6 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan7Vol61 |  | Rack 61 channel 7 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan8Vol61 |  | Rack 61 channel 8 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan9Vol61 |  | Rack 61 channel 9 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan10Vol61 |  | Rack 61 channel 10 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan11Vol61 |  | Rack 61 channel 11 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan12Vol61 |  | Rack 61 channel 12 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan13Vol61 |  | Rack 61 channel 13 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan14Vol61 |  | Rack 61 channel 14 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan15Vol61 |  | Rack 61 channel 15 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan16Vol61 |  | Rack 61 channel 16 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan17Vol61 |  | Rack 61 channel 17 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan18Vol61 |  | Rack 61 channel 18 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan1Vol62 |  | Rack 62 channel 1 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan2Vol62 |  | Rack 62 channel 2 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan3Vol62 |  | Rack 62 channel 3 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan4Vol62 |  | Rack 62 channel 4 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan5Vol62 |  | Rack 62 channel 5 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan6Vol62 |  | Rack 62 channel 6 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan7Vol62 |  | Rack 62 channel 7 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan8Vol62 |  | Rack 62 channel 8 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan9Vol62 |  | Rack 62 channel 9 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan10Vol62 |  | Rack 62 channel 10 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan11Vol62 |  | Rack 62 channel 11 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan12Vol62 |  | Rack 62 channel 12 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan13Vol62 |  | Rack 62 channel 13 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan14Vol62 |  | Rack 62 channel 14 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan15Vol62 |  | Rack 62 channel 15 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan16Vol62 |  | Rack 62 channel 16 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan17Vol62 |  | Rack 62 channel 17 volume |  | 0.0 | 120000.0 | 0.44 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_Chan18Vol62 |  | Rack 62 channel 18 volume |  | 0.0 | 120000.0 | 0.53 | m3 | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_ChGAlHH |  | Channels gas loss HH alarms threshold |  | -200.0 | 3000.0 | 3000.0 | % | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_ChGAlTOTP |  | Channels gas loss alarms delay |  | 0.0 | 99999.0 | 1800.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_CN6126PidChSp |  | Rack 61 Chamber pressure regulation setpoint |  | -15 | 15 | 1 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226PidChSp |  | Rack 62 Chamber pressure regulation setpoint |  | -15 | 15 | 1 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126PidORSp |  | Rack 61 rack Relative output pressure regulation setpoint |  | -15 | 15 | 1 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226PidORSp |  | Rack 62 rack Relative output pressure regulation setpoint |  | -15 | 15 | 1 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126PidOASp |  | Rack 61 rack Absolute output pressure regulation setpoint |  | -2000 | 2000 | 1000 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226PidOASp |  | Rack 62 rack Absolute output pressure regulation setpoint |  | -2000 | 2000 | 1000 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_DeviceDt |  | Profibus communication alarm delay |  | 0.0 | 15.0 | 3.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_EPS |  | Racks Ready/Not Ready transition hysteresis parameter |  | 0.0 | 4.0 | 0.3 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_PRegAlTOTP |  | Racks pressure regulation alarms delay |  | 0.0 | 99999.0 | 5.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_PresAlTOTP |  | PTxx24, PTxx25, PTxx26, PTxx04, PDTxx25 - Pressure alarms delay |  | 0.0 | 30.0 | 5.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_PresSPRamp |  | Pressure regulations setpoint ramp |  | 0.0 | 100000.0 | 50.0 | mbar/s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_rack61PInH |  | (RunNotReady/RunReady) PTxx24 - Rack 61 ready evt input pressure H threshold |  | -10.0 | 10.0 | 6.5 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_rack62PInH |  | (RunNotReady/RunReady) PTxx24 - Rack 62 ready evt input pressure H threshold |  | -10.0 | 10.0 | 6.0 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_rack61PInL |  | (RunNotReady/RunReady) PTxx24 - Rack 61 ready evt input pressure L threshold |  | -10.0 | 10.0 | 2.5 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_rack62PInL |  | (RunNotReady/RunReady) PTxx24 - Rack 62 ready evt input pressure L threshold |  | -10.0 | 10.0 | 2.5 | mbar | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_rack61POutHR |  | (RunNotReady/RunReady) PTxx26 - Rack 61 ready evt output relative pressure H threshold |  | -10 | 10 | 0 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack62POutHR |  | (RunNotReady/RunReady) PTxx26 - Rack 62 ready evt output relative pressure H threshold |  | -10 | 10 | 0 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack61POutLR |  | (RunNotReady/RunReady) PTxx26 - Rack 61 ready evt output relative pressure L threshold |  | -10 | 10 | -2 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack62POutLR |  | (RunNotReady/RunReady) PTxx26 - Rack 62 ready evt output relative pressure L threshold |  | -10 | 10 | -2 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack61PTDev |  | PT6104/x deviation to trigger alarm |  | -10 | 10 | 2 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack62PTDev |  | PT6204/x deviation to trigger alarm |  | -10 | 10 | 2 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack61PTChDev |  | PT6104/x chamber sensors deviation to trigger alarm |  | -10 | 10 | 2 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rack62PTChDev |  | PT6204/x chamber sensors deviation to trigger alarm |  | -10 | 10 | 2 | mbar | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_rackCAirDelay |  | Racks starting sequence delay |  | 0.0 | 1500.0 | 1000.0 | ms | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_RackTOTP |  | Isolation valves operation sequence delay |  | 0.0 | 20.0 | 1.0 | s | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_SignFlowLim |  | (RunNotReady) Significant flows threshold |  | 0.0 | 20000.0 | 50.0 | % | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_SmallFlLimit |  | Minimum significant flow limit to calculate racks total flow stabilization |  | 0.0 | 20000.0 | 30.0 | l/h | ####.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Di_StartupALDt |  | Channels gas loss alarms delay |  | 0 | 99999 | 0 | h | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126StUpK |  | Distribution rack 61 pressure regulator Gain during start-Up |  | 0 | 99999 | 0 |  | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226StUpK |  | Distribution rack 62 pressure regulator Gain during start-Up |  | 0 | 99999 | 0 |  | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126StUpTi |  | Distribution rack 61 pressure regulator Integral time during start-Up |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226StUpTi |  | Distribution rack 62 pressure regulator Integral time during start-Up |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126StUpTd |  | Distribution rack 61 pressure regulator Derivative time during start-Up |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226StUpTd |  | Distribution rack 62 pressure regulator Derivative time during start-Up |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126StUpTds |  | Distribution rack 61 pressure regulator second Derivative time during start-Up |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226StUpTds |  | Distribution rack 62 pressure regulator second Derivative time during start-Up |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126RunK |  | Distribution rack 61 pressure regulator Gain during Run |  | 0 | 99999 | 0 |  | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226RunK |  | Distribution rack 62 pressure regulator Gain during Run |  | 0 | 99999 | 0 |  | ##.# | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126RunTi |  | Distribution rack 61 pressure regulator Integral time during Run |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226RunTi |  | Distribution rack 62 pressure regulator Integral time during Run |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126RunTd |  | Distribution rack 61 pressure regulator Derivative time during Run |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226RunTd |  | Distribution rack 62 pressure regulator Derivative time during Run |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6126RunTds |  | Distribution rack 61 pressure regulator second Derivative time during Run |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_CN6226RunTds |  | Distribution rack 62 pressure regulator second Derivative time during Run |  | 0 | 99999 | 0 |  | ##.### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Di_PCVxx2xRLimDt |  | PCVxx26 Distribution pressure regulation valve limit reached alarm delay |  | 0 | 360 | 20 | s | ### | AnalogParameter |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Xh_AtmPressDt |  | PT0101 - Atmospheric pressure alarm delay |  | 0.0 | 10000.0 | 20.0 | s | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_AtmPressHH |  | PT0101 - Atmospheric pressure HH alarm threshold |  | 0.0 | 1500.0 | 1100.0 | mbar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_AtmPressLL |  | PT0101 - Atmospheric pressure LL alarm threshold |  | 0.0 | 1000.0 | 900.0 | mbar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_AtmPrSenDt |  | PT0101 - Atmospheric pressure transmitter alarm delay |  | 0.0 | 100.0 | 1.0 | h | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_AtPrMax |  | Max. atmospheric pressure parameter for pressure setpoint computation |  | 0.0 | 1200.0 | 980.0 | mbar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_BuPrAlH |  | PT5005 - Buffer pressure H alarm threshold |  | 0.0 | 12.0 | 1.2 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_BuPrAlHH |  | PT5005 - Buffer pressure HH alarm threshold |  | 0.0 | 12.0 | 1.3 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_BuPrAlL |  | PT5005 - Buffer pressure L alarm threshold |  | 0.0 | 10.0 | 0.49 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_BuPrAlLL |  | PT5005 - Buffer pressure LL alarm threshold |  | 0.0 | 10.0 | 0.45 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_BuPrMin |  | Min. buffer pressure parameter for pressure setpoint computation |  | 0.0 | 5000.0 | 600.0 | mbar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_BuPrSenDt |  | PT5005 - Buffer pressure sensor alarm delay |  | 0.0 | 10000.0 | 5.0 | s | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_PDT5030Dt |  | PDT5030 - Exhaust filter clogged alarm delay |  | 0.0 | 10000.0 | 5 | s | ## | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Xh_BuVolComp |  | Buffer volume parameter for pressure setpoint computation |  | 0.0 | 10000.0 | 500.0 | l | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_CiPrAlH |  | PT5011 - Circulation pressure H alarm threshold |  | 0.0 | 12.0 | 2.3 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_ciPrAlHH |  | PT5011 - Circulation pressure HH alarm threshold |  | 0.0 | 12.0 | 2.5 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_ciPrAlL |  | PT5011 - Circulation pressure L alarm threshold |  | 0.0 | 10.0 | 0.55 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_CiPrAlLL |  | PT5011 - Circulation pressure LL alarm threshold |  | 0.0 | 10.0 | 0.001 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_CNPidRamp |  | XMFC5002 - Buffer pressure PID ramp |  | 0.0 | 100.0 | 50.0 | bar/s | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_DetVolComp |  | Detector volume parameter for pressure setpoint computation |  | 0.0 | 120000.0 | 8000.0 | l | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_FailSafeFlSP |  | XMFC5002 - Fail safe flow setpoint |  | 0.0 | 100.0 | 30.0 | l/h | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_MaxPrSP |  | Max. pressure setpoint for pressure setpoint computation |  | 0.0 | 10000.0 | 650.0 | mbar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_MFCC0MaxFlow |  | XMFC5002 - Calibration curve #0 full scale |  | 0.0 | 1000.0 | 120.0 | l/h | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_MFCC1MaxFlow |  | XMFC5002 - Calibration curve #1 full scale |  | 0.0 | 1000.0 | 120.0 | l/h | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_MinPrSP |  | Min. pressure setpoint for pressure setpoint computation |  | 0.0 | 5000.0 | 600.0 | mbar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_PrAlTOTP |  | Exhaust pressure alarms latency (circulation and buffer) |  | 0.0 | 300.0 | 30.0 | s | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_PrRegAlLH |  | Pressure regulation H(-L) alarm threshold |  | 0.0 | 10.0 | 5.0 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_PrRegAlLLHH |  | Pressure regulation HH(-LL) alarm threshold |  | 0.0 | 10.0 | 6.0 | bar | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_PrRegAlTOTP |  | Pressure regulation alarm delay |  | 0.0 | 10000.0 | 5.0 | min | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_TotVolOffset |  | Total exhausted volume computation offset |  | 0.0 | 100000.0 | 1.4 | m3 | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | offset |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_YIC5003_PTTP |  | YC5003 - 3-way valve pulse time |  | 0.0 | 30.0 | 5.0 | s | ####.### | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Xh_RTXMFC5002OfS |  | XMFC5002 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Gs_AfterDiDelay |  | Sequence pause length after Distribution start has been triggered |  | 0.0 | 100000.0 | 1.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AfterMxDelay |  | Sequence pause length after Mixer start has been triggered |  | 0.0 | 100000.0 | 0.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AfterPpDelay |  | Sequence pause length after Pump start has been triggered |  | 0.0 | 100000.0 | 10.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AfterPuDelay |  | Sequence pause length after Purifiers start has been triggered |  | 0.0 | 100000.0 | 0.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AfterXhDelay |  | Sequence pause length after Exhaust start has been triggered |  | 0.0 | 100000.0 | 0.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AlarmStopTOTP |  | Pump, Distribution in Stop, Exhaust not in Run alarms delay |  | 0.0 | 100000.0 | 2.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AtmPressHLim |  | PT0x01 - H limit to reject wrong atmospheric pressure values |  | 0.0 | 1500.0 | 1100.0 | mbar | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_AtmPressLLim |  | PT0x01 - L limit to reject wrong atmospheric pressure values |  | 0.0 | 1000.0 | 900.0 | mbar | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_DeviceDt |  | Profibus communication alarm delay |  | 0.0 | 100000.0 | 2.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_GasLIntPeriod |  | Gas loss integration reset timeout |  | 0.0 | 100000.0 | 3.0 | h | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_MxNotInCompDt |  | Mixer not in compliant state alarm delay |  | 0.0 | 100000.0 | 30.0 | s | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_MxNotInRunDt |  | Mixer not in Run alarm delay |  | 0.0 | 100000.0 | 6.0 | h | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_PSAADt |  | Power supply module alarm delay |  | 0.0 | 100000.0 | 60 | s | # | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Gs_PuNotInNRunDt |  | Purifier not in Nominal Run alarm delay |  | 0.0 | 100000.0 | 6.0 | h | ####.### | AnalogParameter |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Gs_SpareAP1 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP2 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP3 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP4 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP5 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP6 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP7 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP8 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP9 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP10 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP11 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP12 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP13 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP14 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP15 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP16 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP17 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP18 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP19 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Gs_SpareAP20 |  | Spare APAR |  | 0.0 | 100.0 | 0 |  | #.# | AnalogParameter |  |  |  |  | TOF_Details | TOF_Details |  |  | No |  |  |  |  | No | 0.0
ALITOF_Mx_DeviceDt |  | Profibus communication alarm delay |  | 0.0 | 60.0 | 5.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_DirectStabDt |  | (Direct) Time required to stabilize flows regulations |  | 0.0 | 60.0 | 3.0 | min | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_ExtFlamGasDt |  | ZSH9119 - External HW interlock alarm delay |  | 0.0 | 60.0 | 10.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_FillingDt |  | Time required to fill pipes in front of MFCs |  | 0.0 | 60.0 | 1.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_FillReqVol |  | (Fill) Volume required to complete filling |  | 0.0 | 150000.0 | 1000.0 | m3 | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_FillStabDt |  | (Fill) Time required to stabilize ratios and flow regulations |  | 0.0 | 60.0 | 3.0 | min | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_FlowDt |  | All lines - Flow regulation alarm delay |  | 0.0 | 60.0 | 2.0 | min | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FRegDsLH |  | Line 1 - (Direct Stable) Flow regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 2.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2FRegDsLH |  | Line 2 - (Direct Stable) Flow regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 2.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3FRegDsLH |  | Line 3 - (Direct Stable) Flow regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 2.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FRegDsLLHH |  | Line 1 - (Direct Stable) Flow regulation HH(-LL) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2FRegDsLLHH |  | Line 2 - (Direct Stable) Flow regulation HH(-LL) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3FRegDsLLHH |  | Line 3 - (Direct Stable) Flow regulation HH(-LL) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FRegPsL |  | Line 1 - (Purge Stable) Flow regulation L alarm threshold |  | -100.0 | 10.0 | 10.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2FRegPsL |  | Line 2 - (Purge Stable) Flow regulation L alarm threshold |  | -100.0 | 10.0 | 10.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3FRegPsL |  | Line 3 - (Purge Stable) Flow regulation L alarm threshold |  | -100.0 | 10.0 | 10.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FRegPsLL |  | Line 1 - (Purge Stable) Flow regulation LL alarm threshold |  | -100.0 | 5.0 | 5.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2FRegPsLL |  | Line 2 - (Purge Stable) Flow regulation LL alarm threshold |  | -100.0 | 5.0 | 5.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3FRegPsLL |  | Line 3 - (Purge Stable) Flow regulation LL alarm threshold |  | -100.0 | 5.0 | 5.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1HFRamp |  | XMFC1109 - Flow setpoint ramping |  | 0.0 | 1234.56 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2HFRamp |  | XMFC1209 - Flow setpoint ramping |  | 0.0 | 1234.56 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3HFRamp |  | XMFC1309 - Flow setpoint ramping |  | 0.0 | 1234.56 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1LFRamp |  | XMFC1106 - Flow setpoint ramping |  | 0.0 | 1234.56 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2LFRamp |  | XMFC1206 - Flow setpoint ramping |  | 0.0 | 1234.56 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3LFRamp |  | XMFC1306 - Flow setpoint ramping |  | 0.0 | 1234.56 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1MFC6C0FuScl |  | XMFC1106 - Calibration curve 0 full scale |  | 0.0 | 1234.56 | 264.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1MFC6C1FuScl |  | XMFC1106 - Calibration curve 1 full scale |  | 0.0 | 1234.56 | 264.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2MFC6C0FuScl |  | XMFC1206 - Calibration curve 0 full scale |  | 0.0 | 1234.56 | 18.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3MFC6C0FuScl |  | XMFC1306 - Calibration curve 0 full scale |  | 0.0 | 1234.56 | 18.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1MFC9C0FuScl |  | XMFC1109 - Calibration curve 0 full scale |  | 0.0 | 4380.0 | 2400.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1MFC9C1FuScl |  | XMFC1109 - Calibration curve 1 full scale |  | 0.0 | 4380.0 | 2400.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2MFC9C0FuScl |  | XMFC1209 - Calibration curve 0 full scale |  | 0.0 | 1234.56 | 240.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3MFC9C0FuScl |  | XMFC1309 - Calibration curve 0 full scale |  | 0.0 | 1234.56 | 180.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1NotRelDt |  | XMFC1106 - Flow not reliable alarm delay |  | 0.0 | 90.0 | 90.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2NotRelDt |  | XMFC1206 - Flow not reliable alarm delay |  | 0.0 | 90.0 | 90.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3NotRelDt |  | XMFC1306 - Flow not reliable alarm delay |  | 0.0 | 90.0 | 90.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1NotRelH |  | XMFC1106 - Flow not reliable H alarm threshold |  | 0.0 | 120.0 | 103.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2NotRelH |  | XMFC1206 - Flow not reliable H alarm threshold |  | 0.0 | 120.0 | 103.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3NotRelH |  | XMFC1306 - Flow not reliable H alarm threshold |  | 0.0 | 120.0 | 103.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1NotRelHH |  | XMFC1106 - Flow not reliable HH alarm threshold |  | 0.0 | 120.0 | 105.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2NotRelHH |  | XMFC1206 - Flow not reliable HH alarm threshold |  | 0.0 | 120.0 | 105.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3NotRelHH |  | XMFC1306 - Flow not reliable HH alarm threshold |  | 0.0 | 120.0 | 105.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1NotRelL |  | XMFC1106 - Flow not reliable L alarm threshold |  | 0.0 | 100.0 | 0.8 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2NotRelL |  | XMFC1206 - Flow not reliable L alarm threshold |  | 0.0 | 100.0 | 0.8 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3NotRelL |  | XMFC1306 - Flow not reliable L alarm threshold |  | 0.0 | 100.0 | 0.8 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1NotRelLL |  | XMFC1106 - Flow not reliable LL alarm threshold |  | 0.0 | 100.0 | 0.5 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2NotRelLL |  | XMFC1206 - Flow not reliable LL alarm threshold |  | 0.0 | 100.0 | 0.5 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3NotRelLL |  | XMFC1306 - Flow not reliable LL alarm threshold |  | 0.0 | 100.0 | 0.5 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1PressDt |  | PT1103 - Low pressure L alarm delay |  | 0.0 | 20.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2PressDt |  | PT1203 - Low pressure L alarm delay |  | 0.0 | 20.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3PressDt |  | PT1303 - Low pressure L alarm delay |  | 0.0 | 20.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1PressL |  | PT1103 - Low pressure L alarm threshold |  | 0.0 | 100000.0 | 1.3 | bar | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2PressL |  | PT1203 - Low pressure L alarm threshold |  | 0.0 | 100000.0 | 1.3 | bar | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3PressL |  | PT1303 - Low pressure L alarm threshold |  | 0.0 | 100000.0 | 1.5 | bar | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1PressLL |  | PT1103 - Low pressure LL alarm threshold |  | 0.0 | 100000.0 | 1.0 | bar | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2PressLL |  | PT1203 - Low pressure LL alarm threshold |  | 0.0 | 100000.0 | 1.0 | bar | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3PressLL |  | PT1303 - Low pressure LL alarm threshold |  | 0.0 | 100000.0 | 1.1 | bar | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1RRegDt |  | Line 1 - (Fill/Run) Ratio regulation alarm delay |  | 0.0 | 100.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2RRegDt |  | Line 2 - (Fill/Run) Ratio regulation alarm delay |  | 0.0 | 100.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3RRegDt |  | Line 3 - (Fill/Run) Ratio regulation alarm delay |  | 0.0 | 100.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1RRegStLH |  | Line 1 - (Fill/Run Stable) Ratio regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 1.5 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2RRegStLH |  | Line 2 - (Fill/Run Stable) Ratio regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 1.5 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3RRegStLH |  | Line 3 - (Fill/Run Stable) Ratio regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 1.5 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1RRegStLLHH |  | Line 1 - (Fill/Run Stable) Ratio regulation HH(-LL) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2RRegStLLHH |  | Line 2 - (Fill/Run Stable) Ratio regulation HH(-LL) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3RRegStLLHH |  | Line 3 - (Fill/Run Stable) Ratio regulation HH(-LL) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1RRegUnLH |  | Line 1 - (Fill/Run Unstable) Ratio regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2RRegUnLH |  | Line 2 - (Fill/Run Unstable) Ratio regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3RRegUnLH |  | Line 3 - (Fill/Run Unstable) Ratio regulation H(-L) alarm threshold |  | 0.0 | 100.0 | 3.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2DirFlowSp |  | (Direct) Line 2 flow setpoint |  | 0.0 | 100000.0 | 0.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3DirFlowSp |  | (Direct) Line 3 flow setpoint |  | 0.0 | 100000.0 | 0.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2FillRatioSp |  | (Fill) Line 2 (slave) ratio regulation setpoint |  | 0.0 | 123.45 | 0.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3FillRatioSp |  | (Fill) Line 3 (slave) ratio regulation setpoint |  | 0.0 | 123.45 | 7.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2HFPidRamp |  | CN1209 - PID Setpoint ramp speed |  | 0.0 | 100.0 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3HFPidRamp |  | CN1309 - PID Setpoint ramp speed |  | 0.0 | 100.0 | 50.0 | l/hs | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2LFPidRamp |  | CN1206 - PID Setpoint ramp speed |  | 0.0 | 100.0 | 50.0 | %/s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3LFPidRamp |  | CN1306 - PID Setpoint ramp speed |  | 0.0 | 100.0 | 50.0 | %/s | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2PurgeFlowSp |  | (Purge) Line 2 flow setpoint |  | 0.0 | 100000.0 | 0.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3PurgeFlowSp |  | (Purge) Line 3 flow setpoint |  | 0.0 | 100000.0 | 0.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L2RunRatioSp |  | (Run) Line 2 (slave) ratio regulation setpoint |  | 0.0 | 123.45 | 0.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L3RunRatioSp |  | (Run) Line 3 (slave) ratio regulation setpoint |  | 0.0 | 123.45 | 7.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1DirFlowSp |  | (Direct) Line 1 flow setpoint |  | 0.0 | 100000.0 | 175.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FillFlowSp |  | (Fill) Line 1 (master) flow setpoint |  | 0.0 | 100000.0 | 1000.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FlowFsRsL |  | XMFC1106 - (Fill/Run Stable) Master gas flow L alarm threshold |  | 0.0 | 100.0 | 1.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FlowFsRsLL |  | XMFC1106 - (Fill/Run Stable) Master gas flow LL alarm threshold |  | 0.0 | 100.0 | 2.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FlowFuRuL |  | XMFC1106 - (Fill/Run Unstable) Master gas flow L alarm threshold |  | 0.0 | 100.0 | 1.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1FlowFuRuLL |  | XMFC1106 - (Fill/Run Unstable) Master gas flow LL alarm threshold |  | 0.0 | 100.0 | 2.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1PurgeFlowSp |  | (Purge) Line 1 flow setpoint |  | 0.0 | 100000.0 | 75.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_L1RunFlowSp |  | (Run) Line 1 (master) flow setpoint |  | 0.0 | 100000.0 | 120.0 | l/h | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | flow |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_MFCCloseDt |  | Time required to close MFCs |  | 0.0 | 60.0 | 1.0 | ms | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_PurgeReqVol |  | (Purge) Volume required to complete purging |  | 0.0 | 500000.0 | 1000.0 | l | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_PurgeStabDt |  | (Purge) Time required to stabilize flows regulations |  | 0.0 | 60.0 | 3.0 | min | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_RTXMFC1206OfS |  | XMFC1206 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_RTXMFC1306OfS |  | XMFC1306 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_RTXMFC1209OfS |  | XMFC1209 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_RTXMFC1309OfS |  | XMFC1309 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_RTXMFC1106OfS |  | XMFC1106 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_RTXMFC1109OfS |  | XMFC1109 - Total running hours computation offset |  | 0.0 | 90000.0 | 0 | h | ####.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_RunStabDt |  | (Run) Time required to stabilize ratio and flows regulations |  | 0.0 | 60.0 | 3.0 | min | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_SmallFlow |  | Small flows threshold (values ignored if below) |  | 0.0 | 100.0 | 1.0 | % | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_TotVolOffset |  | Total volume computation offset |  | 0.0 | 100000.0 | 0.0 | m3 | ####.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Mx_WrongFlowHH |  | Evaporator Heater HH alarm threshold |  | 0.0 | 500.0 | 20 | C | ##.# | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206StUpKc |  | CN1206 – Kc for XMFC1206 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306StUpKc |  | CN1306 – Kc for XMFC1306 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206StUpTi |  | CN1206 – Ti for XMFC1206 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306StUpTi |  | CN1306 – Ti for XMFC1306 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206StUpTd |  | CN1206 – Td for XMFC1206 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306StUpTd |  | CN1306 – Td for XMFC1306 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206StUpTds |  | CN1206 – Tds for XMFC1206 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306StUpTds |  | CN1306 – Tds for XMFC1306 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209StUpKc |  | CN1209 – Kc for XMFC1209 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309StUpKc |  | CN1309 – Kc for XMFC1309 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209StUpTi |  | CN1209 – Ti for XMFC1209 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309StUpTi |  | CN1309 – Ti for XMFC1309 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209StUpTd |  | CN1209 – Td for XMFC1209 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309StUpTd |  | CN1309 – Td for XMFC1309 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209StUpTds |  | CN1209 – Tds for XMFC1209 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309StUpTds |  | CN1309 – Tds for XMFC1309 flow regulation Start-Up |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206RunKc |  | CN1206 – Kc for XMFC1206 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306RunKc |  | CN1306 – Kc for XMFC1306 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206RunTi |  | CN1206 – Ti for XMFC1206 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306RunTi |  | CN1306 – Ti for XMFC1306 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206RunTd |  | CN1206 – Td for XMFC1206 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306RunTd |  | CN1306 – Td for XMFC1306 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1206RunTds |  | CN1206 – Tds for XMFC1206 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1306RunTds |  | CN1306 – Tds for XMFC1306 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209RunKc |  | CN1209 – Kc for XMFC1209 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309RunKc |  | CN1309 – Kc for XMFC1309 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.## | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209RunTi |  | CN1209 – Ti for XMFC1209 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309RunTi |  | CN1309 – Ti for XMFC1309 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209RunTd |  | CN1209 – Td for XMFC1209 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309RunTd |  | CN1309 – Td for XMFC1309 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1209RunTds |  | CN1209 – Tds for XMFC1209 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Mx_CN1309RunTds |  | CN1309 – Tds for XMFC1309 flow regulation Run |  | 0.0 | 100.0 | 0 |  | #.### | AnalogParameter |  |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0 |  |  |  | No | 0.0
ALITOF_Pp_RunStabDt |  | (Starting) Time required to complete the starting activity |  | 0.0 | 10.0 | 5.0 | min | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PressRegDt |  | Pressure regulation alarm delay |  | 0.0 | 600.0 | 3.0 | s | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PressRegHL |  | Pressure regulation H(-L) alarm thresholds |  | 0.0 | 4.0 | 2.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PressRegHHLL |  | Pressure regulation HH(-LL) alarm thresholds |  | 0.0 | 5.0 | 3.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_RnDfltPSp |  | Pressure regulation set point with PTxx04 sensor |  | -10.0 | 10.0 | -10.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_SWPressDt |  | PT4004 - Soft. pressure alarm delay |  | 0.0 | 240.0 | 3.0 | s | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_SWPressH |  | PT4004 - Soft. pressure H alarm threshold |  | 0.0 | 30.0 | 10.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_SWPressHH |  | PT4004 - Soft. pressure HH alarm threshold |  | 0.0 | 30.0 | 20.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_SWPressL |  | PT4004 - Soft. pressure L alarm threshold |  | -30.0 | 0.0 | -15.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_SWPressLL |  | PT4004 - Soft. pressure LL alarm threshold |  | -50.0 | 0.0 | -50.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PmPPressDt |  | PT4i01/j - Membranes pressures alarms delay |  | 0.0 | 600.0 | 120.0 | s | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PmPPressH |  | PT4i01/j - Membranes pressures H alarm threshold |  | 0.0 | 3.4 | 0.4 | bar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PmPPressHH |  | PT4i01/j - Membranes pressures HH alarm threshold |  | 0.0 | 4.5 | 0.5 | bar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PmPPressL |  | PT4i01/j - Membranes pressures L alarm threshold |  | -1.0 | 2.3 | -0.2 | bar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PmPPressLL |  | PT4i01/j - Membranes pressures LL alarm threshold |  | -1.0 | 1.2 | -0.5 | bar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_RT1Offset |  | PUMP4101 - Total running hours computation offset |  | 0.0 | 90000.0 | 0.0 | h | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_RT2Offset |  | PUMP4201 - Total running hours computation offset |  | 0.0 | 90000.0 | 0.0 | h | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PIDSpMax |  | PV4003 - Pressure regulation max setpoint |  | -10.0 | 10.0 | 2.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PIDSpMin |  | PV4003 - Pressure regulation min setpoint |  | -12.0 | 10.0 | -12.0 | mbar | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PIDRamp |  | PV4003 - Pressure regulation PID ramp parameter |  | 0.0 | 1000.0 | 2.0 | mbar/s | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_TooHot1H |  | TE4i01/1 - Pump too hot H alarm threshold |  | 0.0 | 149.0 | 42.0 | C | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_TooHot1HH |  | TE4i01/1 - Pump too hot HH alarm threshold |  | 0.0 | 150.0 | 55.0 | C | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_TooHotDt |  | TE4i01/j - Pumps temperatures alarms delay |  | 0.0 | 240.0 | 5.0 | min | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PmpUpRunDt |  | YV4002 - (Starting) Time after which the bypass valve shall be closed |  | 0.0 | 5.0 | 5.0 | s | ####.### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_Pp_PV4003RLimDt |  | Pump pressure regulation valve limit reached alarm delay |  | 0.0 | 1000 | 180 | s | ### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003StUpKc |  | CN4003 – Kc for Pump Pressure regulation Start-Up |  | 0.0 | 100.0 | 2 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003StUpTi |  | CN4003 – Ti for Pump Pressure regulation Start-Up |  | 0.0 | 100.0 | 5 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003StUpTd |  | CN4003 – Td for Pump Pressure regulation Start-Up |  | 0.0 | 100.0 | 0 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003StUpTds |  | CN4003 – Tds for Pump Pressure regulation Start-Up |  | 0.0 | 100.0 | 0 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003RunKc |  | CN4003 – Kc for Pump Pressure regulation Run |  | 0.0 | 100.0 | 2 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003RunTi |  | CN4003 – Ti for Pump Pressure regulation Run |  | 0.0 | 100.0 | 5 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003RunTd |  | CN4003 – Td for Pump Pressure regulation Run |  | 0.0 | 100.0 | 0 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_CN4003RunTds |  | CN4003 – Tds for Pump Pressure regulation Run |  | 0.0 | 100.0 | 0 |  | ##.## | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_PDT4020Dt |  | Pump module outlet filter clogged alarm delay |  | 0.0 | 1000 | 60 | s | ### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_Pp_PUMPDefDisDt |  | Pump Circuit breaker tripped alarm delay |  | 0.0 | 100 | 1 | s | ### | AnalogParameter |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_P1_AlmLatency |  | Valves position alarms delay |  | 0.0 | 100000.0 | 5000.0 | ms | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_BadTRegulH |  | (Regeneration) - Temperature (TEx101/1-2) regulation H (-L) alarm threshold |  | 0.0 | 100000.0 | 230.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_BadTRegulHH |  | (Regeneration) - Temperature (TEx101/1-2) regulation HH (-LL) alarm threshold |  | 0.0 | 100000.0 | 245.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CANmROffset |  | Column A number of regeneration cycles computation offset |  | 0.0 | 100.0 | 23.0 | - | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | Offset |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CBNmROffset |  | Column B number of regeneration cycles computation offset |  | 0.0 | 100.0 | 21.0 | - | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | Offset |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CARunVOffset |  | Column A run total volume offset |  | 0.0 | 10000.0 | 20.0 | m3 | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | Offset |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CBRunVOffset |  | Column B run total volume offset |  | 0.0 | 10000.0 | 0.0 | m3 | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | Offset |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CAPh1OnDt |  | (Prepare for Run/Ph1) - Column A Input valve (YVij03) opening time for pulsing |  | 0.0 | 100000.0 | 0.5 | s | ###.## | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CAPh1OffDt |  | (Prepare for Run/Ph1) - Column A Input valve (YVij03) waiting time between two pulses |  | 0.0 | 100000.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CAPh1PrDelta |  | (Prepare for Run/Ph1 - Column A max pressure difference to complete Ph1 (PT5005 used) |  | 0.0 | 100000.0 | 0.05 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CAPh1Timer |  | (Prepare for Run/Ph1) - Column A max time for phase 1 |  | 10.0 | 100000.0 | 180.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CBPh1OffDt |  | Column B Input valve (YVij03) waiting time between two pulses |  | 0.0 | 100000.0 | 15.0 | s | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CBPh1OnDt |  | (Prepare for Run/Ph1) - Column B Input valve (YVij03) opening time for pulsing |  | 0.0 | 100000.0 | 0.5 | s | ####.## | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CBPh1PrDelta |  | (Prepare for Run/Ph1 - Column B max pressure difference to complete Ph1 (PT5005 used) |  | 0.0 | 100000.0 | 0.05 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CBPh1Timer |  | (Prepare for Run/Ph1) - Column B max time for phase 1 |  | 10.0 | 100000.0 | 180.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CDMaxTime |  | (Cool Down) - Max time for cool down temperature to be reached |  | 0.0 | 100000.0 | 1000.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_ColSynchAlDt |  | Purifier Columns not synchronized alarm |  | 0.0 | 1000.0 | 30 | s | ## | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison |  |  |  |  | No | 0.0
ALITOF_P1_ColumnPrPLim |  | (Prepare for standby) - Completion high pressure (PTxc08) limit |  | 0.0 | 100000.0 | 0.0 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_CoolDownTemp |  | (Cool down,Purge) - Completion low temperature (TEx101/1-2) threshold |  | 0.0 | 100000.0 | 50.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_DeviceDt |  | Profibus communication alarm delay |  | 0.0 | 100000.0 | 2000.0 | ms | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_EvacPress |  | Evacuation pressure threshold to trigger the extraction pump |  | -1.0 | 5.0 | -0.1 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_ExtTHotH |  | (Regeneration) - Internal temperature (TEx101/3) H alarm threshold |  | 0.0 | 100000.0 | 240.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_ExtTHotHH |  | (Regeneration) - Internal temperature (TEx101/3) HH alarm threshold |  | 0.0 | 100000.0 | 250.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_HUpCheckDelay |  | (Heat up) - Slow heating up (TEx101/1-2) alarm delay |  | 0.0 | 100000.0 | 60.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_HUpFirstStepT |  | (Heat up) - Slow heating up (TEx101/1-2) LL temperature alarm threshold |  | 0.0 | 100000.0 | 40.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_HUpMaxTime |  | (Heat Up) - Max time for regeneration temperature to be reached |  | 0.0 | 100000.0 | 240.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_MaxExtTemp |  | (Heat up, Regenaration) - HH temperature (TExc01/2) limit for heater operation |  | 0.0 | 100000.0 | 220.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_NoPurgeAlTOTP |  | (Purge, CoolDown, Standby) - No flow detected in FIS3112 alarm delay |  | 0.0 | 100000.0 | 15000.0 | ms | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_NoRegenAlTOTP |  | (Regeneration) - No flow detected in FIS3112 alarm delay |  | 0.0 | 100000.0 | 15000.0 | ms | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PreHUpTempe |  | (Heat Up) - Temperature (TEx101/1-2) at which pump switch on |  | 0.0 | 100000.0 | 50.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PrepRunP2Time |  | (Prepare For Run/Ph2) - Completion timeout |  | 0.0 | 100000.0 | 300.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PressAdjustDt |  | (Prepare For Run/Ph1) - Delay to allow Column Pressure stabilization after filling pulse |  | 0.0 | 100.0 | 10.0 | s | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PressDelta |  | gap of pressure variation (applied on exhaust pt5005 sensor) |  | 0.0 | 10.0 | 0.0 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PressReadyH |  | (Prepare For Run/Ph1) Column Pressure adjustment H limit |  | -10.0 | 10.0 | 0.5 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PressReadyL |  | (Prepare For Run/Ph1) Column Pressure adjustment L limit |  | -10.0 | 10.0 | 0.4 | bar | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | pressure |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PrStBMaxTime |  | (Prepare for Stand By) - Max time for Standby pressure to be reached |  | 0.0 | 6000000.0 | 6000000.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_PurgPrGasTime |  | (Purge) - Completion timeout |  | 0.0 | 100000.0 | 1.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_RegenTempeSP |  | (Regeneration) - Temperature (TEx101/1-2) regulation setpoint |  | 0.0 | 100000.0 | 220.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_RegenTime |  | (Regeneration) Completion timeout |  | 0.0 | 100000.0 | 720.0 | min | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | delay |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_RunHotH |  | (Run) - Internal temperature TEx101/1-2 H alarm threshold |  | 0.0 | 100000.0 | 60.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_RunHotHH |  | (Run) - Internal temperature TEx101/1-2 HH alarm threshold |  | 0.0 | 100000.0 | 100.0 | C | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details | temperature |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_RunPrSatVoLim |  | (Run Nominal) Columns pre saturation volume threshold |  | 0.0 | 100000.0 | 160.0 | m3 | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0
ALITOF_P1_RunSatVoLim |  | (Run Pre Saturation) Columns saturation volume threshold |  | 0.0 | 100000.0 | 2000.0 | m3 | ####.### | AnalogParameter |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf |  | TOF_Details | TOF_Details |  |  | Old/New Comparison | 0.0 |  |  |  | No | 0.0

## WordStatus
Name | WordStatus
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Word Status Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [6 empty] | SCADADeviceFunctionals |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceParameters |  | SCADADeviceAlarms
[7 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [13 empty] | Alarm Config |  |  |  | Alarm Values
Name | Expert Name | Description | Remarks | Range Min | Range Max | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Pattern | Synoptic | Diagnostic | WWW Link | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | F Range Min | F Range Max | SMS Category | Auto Acknowledge | Masked | Message | Low | Medium | High | Safety
ALITOF_Di_BlckCnt |  | Distribution PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ## | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Di_FCELMBSt1WS |  | Distribution ELMB status 1 |  | 0 | 65535 | 100 |  | 15120 | 0 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCELMBSt2WS |  | Distribution ELMB status 2 |  | 0 | 65535 | 100 |  | 15120 | 1 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCELMBSt3WS |  | Distribution ELMB status 3 |  | 0 | 65535 | 100 |  | 15120 | 2 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack61En1WS |  | Distribution rack 61 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 0 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack62En1WS |  | Distribution rack 62 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 4 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack61En2WS |  | Distribution rack 61 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 1 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack62En2WS |  | Distribution rack 62 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 5 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack61En3WS |  | Distribution rack 61 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 2 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack62En3WS |  | Distribution rack 62 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 6 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack61En4WS |  | Distribution rack 61 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 3 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRack62En4WS |  | Distribution rack 62 flowcell enabled status |  | 0 | 65535 | 100 |  | 15360 | 7 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRackCmd1WS |  | Distribution channel speed rate cmd 1 |  | 0 | 65535 | 100 |  | 15240 | 0 |  |  |  |  | Out |  |  |  | ##### | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRackCmd2WS |  | Distribution channel speed rate cmd 2 |  | 0 | 65535 | 100 |  | 15240 | 1 |  |  |  |  | Out |  |  |  | ##### | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Cmd1WS |  | Distribution rack 61 flowcell command status |  | 0 | 65535 | 100 |  | 15600 | 0 |  |  |  |  | Out |  |  |  | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Cmd2WS |  | Distribution rack 61 flowcell command status |  | 0 | 65535 | 100 |  | 15600 | 1 |  |  |  |  | Out |  |  |  | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Cmd1WS |  | Distribution rack 62 flowcell command status |  | 0 | 65535 | 100 |  | 15600 | 4 |  |  |  |  | Out |  |  |  | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Cmd2WS |  | Distribution rack 62 flowcell command status |  | 0 | 65535 | 100 |  | 15600 | 5 |  |  |  |  | Out |  |  |  | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Err1WS |  | Distribution rack 61 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 0 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Err1WS |  | Distribution rack 62 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 4 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Err2WS |  | Distribution rack 61 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 1 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Err2WS |  | Distribution rack 62 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 5 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Err3WS |  | Distribution rack 61 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 2 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Err3WS |  | Distribution rack 62 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 6 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Err4WS |  | Distribution rack 61 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 3 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Err4WS |  | Distribution rack 62 flowcell error status |  | 0 | 65535 | 100 |  | 15480 | 7 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Nbr1WS |  | Distribution rack 1 flowcell channel nbr Selected 1 |  | 0 | 65535 | 100 |  | 17040 | 0 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Nbr1WS |  | Distribution rack 1 flowcell channel nbr Selected 1 |  | 0 | 65535 | 100 |  | 17040 | 4 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Nbr2WS |  | Distribution rack 1 flowcell channel nbr Selected 2 |  | 0 | 65535 | 100 |  | 17040 | 1 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Nbr2WS |  | Distribution rack 1 flowcell channel nbr Selected 2 |  | 0 | 65535 | 100 |  | 17040 | 5 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Nbr3WS |  | Distribution rack 1 flowcell channel nbr Selected 3 |  | 0 | 65535 | 100 |  | 17040 | 2 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Nbr3WS |  | Distribution rack 1 flowcell channel nbr Selected 3 |  | 0 | 65535 | 100 |  | 17040 | 6 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck61Nbr4WS |  | Distribution rack 1 flowcell channel nbr Selected 4 |  | 0 | 65535 | 100 |  | 17040 | 3 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCRck62Nbr4WS |  | Distribution rack 1 flowcell channel nbr Selected 4 |  | 0 | 65535 | 100 |  | 17040 | 7 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FCWebMasWS |  | Distribution webmas status |  | 0 | 65535 | 100 |  | 15120 | 3 | [8 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | No
ALITOF_Di_FE6102Ch1 |  | Distribution rack 61 channel 1 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 0 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch2 |  | Distribution rack 61 channel 2 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 2 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch3 |  | Distribution rack 61 channel 3 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 4 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch4 |  | Distribution rack 61 channel 4 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 6 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch5 |  | Distribution rack 61 channel 5 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 8 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch6 |  | Distribution rack 61 channel 6 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 10 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch7 |  | Distribution rack 61 channel 7 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 12 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch8 |  | Distribution rack 61 channel 8 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 14 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch9 |  | Distribution rack 61 channel 9 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 16 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch10 |  | Distribution rack 61 channel 10 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 18 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch11 |  | Distribution rack 61 channel 11 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 20 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch12 |  | Distribution rack 61 channel 12 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 22 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch13 |  | Distribution rack 61 channel 13 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 24 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch14 |  | Distribution rack 61 channel 14 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 26 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch15 |  | Distribution rack 61 channel 15 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 28 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch16 |  | Distribution rack 61 channel 16 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 30 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch17 |  | Distribution rack 61 channel 17 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 32 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6102Ch18 |  | Distribution rack 61 channel 18 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 34 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch1 |  | Distribution rack 62 channel 1 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 36 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch2 |  | Distribution rack 62 channel 2 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 38 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch3 |  | Distribution rack 62 channel 3 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 40 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch4 |  | Distribution rack 62 channel 4 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 42 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch5 |  | Distribution rack 62 channel 5 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 44 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch6 |  | Distribution rack 62 channel 6 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 46 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch7 |  | Distribution rack 62 channel 7 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 48 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch8 |  | Distribution rack 62 channel 8 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 50 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch9 |  | Distribution rack 62 channel 9 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 52 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch10 |  | Distribution rack 62 channel 10 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 54 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch11 |  | Distribution rack 62 channel 11 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 56 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch12 |  | Distribution rack 62 channel 12 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 58 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch13 |  | Distribution rack 62 channel 13 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 60 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch14 |  | Distribution rack 62 channel 14 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 62 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch15 |  | Distribution rack 62 channel 15 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 64 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch16 |  | Distribution rack 62 channel 16 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 66 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch17 |  | Distribution rack 62 channel 17 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 68 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6202Ch18 |  | Distribution rack 62 channel 18 flow cell in |  | 0 | 3000 | 100 |  | 15840 | 70 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch1 |  | Distribution rack 61 channel 1 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 1 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch2 |  | Distribution rack 61 channel 2 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 3 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch3 |  | Distribution rack 61 channel 3 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 5 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch4 |  | Distribution rack 61 channel 4 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 7 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch5 |  | Distribution rack 61 channel 5 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 9 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch6 |  | Distribution rack 61 channel 6 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 11 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch7 |  | Distribution rack 61 channel 7 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 13 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch8 |  | Distribution rack 61 channel 8 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 15 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch9 |  | Distribution rack 61 channel 9 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 17 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch10 |  | Distribution rack 61 channel 10 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 19 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch11 |  | Distribution rack 61 channel 11 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 21 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch12 |  | Distribution rack 61 channel 12 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 23 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch13 |  | Distribution rack 61 channel 13 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 25 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch14 |  | Distribution rack 61 channel 14 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 27 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch15 |  | Distribution rack 61 channel 15 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 29 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch16 |  | Distribution rack 61 channel 16 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 31 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch17 |  | Distribution rack 61 channel 17 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 33 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6106Ch18 |  | Distribution rack 61 channel 18 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 35 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch1 |  | Distribution rack 62 channel 1 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 37 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch2 |  | Distribution rack 62 channel 2 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 39 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch3 |  | Distribution rack 62 channel 3 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 41 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch4 |  | Distribution rack 62 channel 4 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 43 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch5 |  | Distribution rack 62 channel 5 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 45 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch6 |  | Distribution rack 62 channel 6 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 47 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch7 |  | Distribution rack 62 channel 7 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 49 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch8 |  | Distribution rack 62 channel 8 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 51 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch9 |  | Distribution rack 62 channel 9 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 53 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch10 |  | Distribution rack 62 channel 10 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 55 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch11 |  | Distribution rack 62 channel 11 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 57 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch12 |  | Distribution rack 62 channel 12 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 59 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch13 |  | Distribution rack 62 channel 13 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 61 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch14 |  | Distribution rack 62 channel 14 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 63 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch15 |  | Distribution rack 62 channel 15 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 65 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch16 |  | Distribution rack 62 channel 16 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 67 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch17 |  | Distribution rack 62 channel 17 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 69 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_FE6206Ch18 |  | Distribution rack 62 channel 18 flow cell out |  | 0 | 3000 | 100 |  | 15840 | 71 | [7 empty] | l/h | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 0.3 |  |  |  | Absolute | 0.3 | 0 | 300
ALITOF_Di_GasLosR61Ch1 |  | Distribution rack 61 chan 1 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch2 |  | Distribution rack 61 chan 2 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch3 |  | Distribution rack 61 chan 3 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch4 |  | Distribution rack 61 chan 4 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch5 |  | Distribution rack 61 chan 5 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch6 |  | Distribution rack 61 chan 6 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch7 |  | Distribution rack 61 chan 7 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch8 |  | Distribution rack 61 chan 8 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch9 |  | Distribution rack 61 chan 9 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch10 |  | Distribution rack 61 chan 10 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch11 |  | Distribution rack 61 chan 11 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch12 |  | Distribution rack 61 chan 12 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch13 |  | Distribution rack 61 chan 13 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch14 |  | Distribution rack 61 chan 14 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch15 |  | Distribution rack 61 chan 15 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch16 |  | Distribution rack 61 chan 16 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch17 |  | Distribution rack 61 chan 17 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR61Ch18 |  | Distribution rack 61 chan 18 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch1 |  | Distribution rack 62 chan 1 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch2 |  | Distribution rack 62 chan 2 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch3 |  | Distribution rack 62 chan 3 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch4 |  | Distribution rack 62 chan 4 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch5 |  | Distribution rack 62 chan 5 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch6 |  | Distribution rack 62 chan 6 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch7 |  | Distribution rack 62 chan 7 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch8 |  | Distribution rack 62 chan 8 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch9 |  | Distribution rack 62 chan 9 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch10 |  | Distribution rack 62 chan 10 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch11 |  | Distribution rack 62 chan 11 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch12 |  | Distribution rack 62 chan 12 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch13 |  | Distribution rack 62 chan 13 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch14 |  | Distribution rack 62 chan 14 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch15 |  | Distribution rack 62 chan 15 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch16 |  | Distribution rack 62 chan 16 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch17 |  | Distribution rack 62 chan 17 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_GasLosR62Ch18 |  | Distribution rack 62 chan 18 gas loss |  | -500 | 500 | [11 empty] | % | ##.# | Word2AnalogStatus |  | ALITOF/ALITOF_DistribFlowCell62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 6.0 |  |  |  | Absolute | 0.1 | -50 | 50
ALITOF_Di_ModStepWS |  | Distribution PCO state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 1=Stop,15=ComPurgeStart,20=ComPurgeReady,25=RunStarting,30=RunNotReady,35=RunReady | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Di_PpMvSel61WS |  | Distribution Cn4003 MV selected from PT6104/1,PT6104/2 and PT6126 |  | 0 | 65535 | [12 empty] | ##### | WordStatus | 1=PT6104/1,2=PT6104/2,3=PT6126 | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 10 | [5 empty] | No | 0.0
ALITOF_Di_PpMvSel62WS |  | Distribution Cn4003 MV selected from PT6204/1,PT6204/2 and PT6226 |  | 0 | 65535 | [12 empty] | ##### | WordStatus | 1=PT6204/1,2=PT6204/2,3=PT6226 | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 10 | [5 empty] | No | 0.0
ALITOF_Di_Rack61BlckCnt |  | Distribution rack 61 PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ## | WordStatus |  | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Di_Rack62BlckCnt |  | Distribution rack 62 PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ## | WordStatus |  | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Di_Rack61StepWS |  | Distribution rack 61 state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 1=Stop,5=IndPurgeStart,7=IndPurgeStart2,10=IndPurgeReady,15=StartComPurge,17=StartComPurge2,20=ComPurgeReady,25=RunStart,27=RunStart2,30=RunNotReady,35=RunReady | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Di_Rack62StepWS |  | Distribution rack 62 state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 1=Stop,5=IndPurgeStart,7=IndPurgeStart2,10=IndPurgeReady,15=StartComPurge,17=StartComPurge2,20=ComPurgeReady,25=RunStart,27=RunStart2,30=RunNotReady,35=RunReady | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Di_CN6126MVWS |  | Distribution rack 61 pressure sensor selected for regulation |  | 0 | 6 | [12 empty] | ## | WordStatus | 1= PT6104, 2= PT6105, 3= PT6125 + GS_RefAtmPrUXAS, 4= PT6125, 5= PT6126 + GS_RefAtmPrUXAS, 6= PT6126 | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 10 | [5 empty] | No | 0.0
ALITOF_Di_CN6226MVWS |  | Distribution rack 62 pressure sensor selected for regulation |  | 0 | 6 | [12 empty] | ## | WordStatus | 1= PT6204, 2= PT6205, 3= PT6225 + GS_RefAtmPrUXAS, 4= PT6225, 5= PT6226 + GS_RefAtmPrUXAS, 6= PT6226 | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 10 | [5 empty] | No | 0.0
ALITOF_Xh_StepperWS |  | Exhaust current stepper state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,1=Stop,2=Recirculating,3=Venting | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Xh_BlckCnt |  | ExhaustPCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Gs_BlckCnt |  | GasSystem PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Gs_GsStepWS |  | GasSystem system stepper |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 100=Stop,1=Purge1,2=Purge2,3=Purge3,4=Purge4,5=Purge5,6=Purging,7=Recup1,8=Recup2,9=Recup3,10=Recup4,11=Recup5,12=Recup51,13=Recup52,14=Recup6,15=Recuperating,16=Run1,17=Run2,18=Run3,19=Run4,20=Run5,21=Run6,22=Run61,23=Run62,24=Run7,25=Run,26=Fill1,27=Fill2,28=Fill3,29=Fill4,30=Fill5,31=Fill6,32=Fill7,33=Filling,34=FillCompletion |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Gs_SpareWS1 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS2 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS3 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS4 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS5 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS6 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS7 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS8 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS9 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Gs_SpareWS10 |  | Spare WS |  | 0 | 100 | [12 empty] | ##### | WordStatus |  |  |  |  | TOF_Details | TOF_Details |  |  | No | 10 | [5 empty] | No | 0.0
ALITOF_Mx_StepperWS |  | Mixer PCO current state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,1=Stop,2=FillPrepare,3=PurgeE,4=RunPrepare,5=DirectE,6=FillUnstable,7=PurgeUnstable,8=RunUnstable,9=DirectUnstable,10=Fill,11=Purge,12=Run,13=Direct,14=RunHalt | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_L1StepperWS |  | Mixer L1 PCO current state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,1=Stop,2=Closing,3=LowFlowOpen,4=LowFlowRegulation,5=HighFlowOpen,6=HighFlowRegulation | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_L2StepperWS |  | Mixer L2 PCO current state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,1=Stop,2=Closing,3=LowFlowOpen,4=LowFlowRegulation,5=HighFlowOpen,6=HighFlowRegulation | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_L3StepperWS |  | Mixer L3 PCO current state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,1=Stop,2=Closing,3=LowFlowOpen,4=LowFlowRegulation,5=HighFlowOpen,6=HighFlowRegulation | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_BlckCnt |  | Mixer PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_L1BlckCnt |  | Mixer L1PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_L2BlckCnt |  | Mixer L2PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Mx_L3BlckCnt |  | Mixer L3PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Pp_StepperWS |  | stepper state |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,1=Stop,2=Starting,3=Run | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_Pp_BlckCnt |  | PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_PuCAStepWS |  | Purifier1 col A PCO stepper |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,100=Stop,1=StandBy,2=NominalRun,3=RegPurge,4=CoolDown,5=ColumnPurge,6=PrepRunPh1,7=PrepRunPh2,8= PreSaturated,9=HeatUp,10=Regeneration,11=PreStandBy,12=Ph1FillOn,13=Ph1FillOff | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_PuCBStepWS |  | Purifier1 col B PCO stepper |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,100=Stop,1=StandBy,2=NominalRun,3=RegPurge,4=CoolDown,5=ColumnPurge,6=PrepRunPh1,7=PrepRunPh2,8= PreSaturated,9=HeatUp,10=Regeneration,11=PreStandBy,12=Ph1FillOn,13=Ph1FillOff | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_CABlckCnt |  | Purifier1 col A PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_CBBlckCnt |  | Purifier1 col B PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_PuStepWS |  | Purifier1 PCO stepper |  | 0 | 65535 | [12 empty] | ###### | WordStatus | 0=Undefined,100=Stop,2=NominalRun,20=CA_Run,30=CB_Run,40=CACB_Run,50=FreeRun | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_BlckCnt |  | Purifier1PCO count of Quantity of blocked Alarm/interlock |  | 0 | 65535 | [12 empty] | ##### | WordStatus |  | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 1.0 | [5 empty] | No
ALITOF_P1_EvacPressB |  | Purifier1 Evacuation pressure reached bit |  | 0 | 1 | [12 empty] | ##### | WordStatus | 0=FALSE,1=TRUE | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison OR Time | 10 | [5 empty] | No | 0.0

## AnalogStatus
Name | AnalogStatus
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Analog Status Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms
[8 empty] | FEChannel | [16 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds
Name | Expert Name | Description | Remarks | Range Min | Range Max | Filtering Time (s) | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm
ALITOF_Di_61TotFlowAS |  | Distribution rack 61 total flow status |  | 0 | 10000 | [12 empty] | l/h | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 1.0 |  |  |  | Absolute | 1.0
ALITOF_Di_62TotFlowAS |  | Distribution rack 62 total flow status |  | 0 | 10000 | [12 empty] | l/h | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 1.0 |  |  |  | Absolute | 1.0
ALITOF_Di_TotFlowAS |  | Distribution total flow status of all racks |  | 0 | 100000 | [12 empty] | l/h | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 10.0 |  |  |  | Absolute | 10.0
ALITOF_Di_Ch1VoReR61AS |  | Distribution volume replacement rate rack 61 chan 1 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch2VoReR61AS |  | Distribution volume replacement rate rack 61 chan 2 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch3VoReR61AS |  | Distribution volume replacement rate rack 61 chan 3 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch4VoReR61AS |  | Distribution volume replacement rate rack 61 chan 4 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch5VoReR61AS |  | Distribution volume replacement rate rack 61 chan 5 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch6VoReR61AS |  | Distribution volume replacement rate rack 61 chan 6 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch7VoReR61AS |  | Distribution volume replacement rate rack 61 chan 7 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch8VoReR61AS |  | Distribution volume replacement rate rack 61 chan 8 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch9VoReR61AS |  | Distribution volume replacement rate rack 61 chan 9 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch10VoReR61AS |  | Distribution volume replacement rate rack 61 chan 10 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch11VoReR61AS |  | Distribution volume replacement rate rack 61 chan 11 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch12VoReR61AS |  | Distribution volume replacement rate rack 61 chan 12 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch13VoReR61AS |  | Distribution volume replacement rate rack 61 chan 13 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch14VoReR61AS |  | Distribution volume replacement rate rack 61 chan 14 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch15VoReR61AS |  | Distribution volume replacement rate rack 61 chan 15 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch16VoReR61AS |  | Distribution volume replacement rate rack 61 chan 16 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch17VoReR61AS |  | Distribution volume replacement rate rack 61 chan 17 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch18VoReR61AS |  | Distribution volume replacement rate rack 61 chan 18 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch1VoReR62AS |  | Distribution volume replacement rate rack 62 chan 1 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch2VoReR62AS |  | Distribution volume replacement rate rack 62 chan 2 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch3VoReR62AS |  | Distribution volume replacement rate rack 62 chan 3 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch4VoReR62AS |  | Distribution volume replacement rate rack 62 chan 4 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch5VoReR62AS |  | Distribution volume replacement rate rack 62 chan 5 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch6VoReR62AS |  | Distribution volume replacement rate rack 62 chan 6 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch7VoReR62AS |  | Distribution volume replacement rate rack 62 chan 7 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch8VoReR62AS |  | Distribution volume replacement rate rack 62 chan 8 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch9VoReR62AS |  | Distribution volume replacement rate rack 62 chan 9 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch10VoReR62AS |  | Distribution volume replacement rate rack 62 chan 10 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch11VoReR62AS |  | Distribution volume replacement rate rack 62 chan 11 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch12VoReR62AS |  | Distribution volume replacement rate rack 62 chan 12 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch13VoReR62AS |  | Distribution volume replacement rate rack 62 chan 13 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch14VoReR62AS |  | Distribution volume replacement rate rack 62 chan 14 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch15VoReR62AS |  | Distribution volume replacement rate rack 62 chan 15 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch16VoReR62AS |  | Distribution volume replacement rate rack 62 chan 16 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch17VoReR62AS |  | Distribution volume replacement rate rack 62 chan 17 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_Ch18VoReR62AS |  | Distribution volume replacement rate rack 62 chan 18 |  | 0 | 72 | [12 empty] | h | #.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.44 |  |  |  | Absolute | 1.44
ALITOF_Di_61FlowStaAS |  | Distribution rack 61 total flow stabilization of flow cell |  | -100 | 100 | [12 empty] | % | ##.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 2.0 |  |  |  | Absolute | 2.0
ALITOF_Di_62FlowStaAS |  | Distribution rack 62 total flow stabilization of flow cell |  | -100 | 100 | [12 empty] | % | ##.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 2.0 |  |  |  | Absolute | 2.0
ALITOF_Di_CN6126K |  | Distribution rack 61 pressure regulator Gain |  | -100.0 | 100.0 | [13 empty] | ##.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.01
ALITOF_Di_CN6226K |  | Distribution rack 62 pressure regulator Gain |  | -100.0 | 100.0 | [13 empty] | ##.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.01
ALITOF_Di_CN6126Ti |  | Distribution rack 61 pressure regulator Integral Time |  | -100.0 | 100.0 | [13 empty] | ##.### | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6226Ti |  | Distribution rack 62 pressure regulator Integral Time |  | -100.0 | 100.0 | [13 empty] | ##.### | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6126Td |  | Distribution rack 61 pressure regulator Derivative Time |  | -100.0 | 100.0 | [13 empty] | ##.### | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6226Td |  | Distribution rack 62 pressure regulator Derivative Time |  | -100.0 | 100.0 | [13 empty] | ##.### | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6126Tds |  | Distribution rack 61 pressure regulator second Derivative Time |  | -100.0 | 100.0 | [13 empty] | ##.### | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6226Tds |  | Distribution rack 62 pressure regulator second Derivative Time |  | -100.0 | 100.0 | [13 empty] | ##.### | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details | PID |  | Deadband AND Time | 1800 | Absolute | 1.0 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6126PidAuSp |  | Distribution rack 61 pressure regulation setpoint |  | -100 | 100.0 | [12 empty] | mbar | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 0.001 |  |  |  | Absolute | 0.001
ALITOF_Di_CN6226PidAuSp |  | Distribution rack 62 pressure regulation setpoint |  | -100 | 100.0 | [12 empty] | mbar | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 0.001 |  |  |  | Absolute | 0.001
ALITOF_Di_Rack61PresDev |  | Distribution rack 61 pressure regulation deviation |  | -100 | 100.0 | [12 empty] | mbar | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 0.001 |  |  |  | Absolute | 0.001
ALITOF_Di_Rack62PresDev |  | Distribution rack 62 pressure regulation deviation |  | -100 | 100.0 | [12 empty] | mbar | ###.# | AnalogStatus |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 0.001 |  |  |  | Absolute | 0.001
ALITOF_Xh_PrSetPointAS |  | Exhaust computed pressure setpoint |  | 0 | 10 | [12 empty] | bar | #.### | AnalogStatus | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.01 |  |  |  | Absolute | 0.01
ALITOF_Xh_PrRDAS |  | Exhaust pressure regulation deviation |  | 0 | 10 | [12 empty] | bar | ##.# | AnalogStatus | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Absolute | 0.5
ALITOF_Xh_BuffPTDev |  | Exhaust buffer pressure deviation |  | 0.0 | 10.0 | [12 empty] | bar | ##.# | AnalogStatus | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details | pressure |  | No | [6 empty] | Absolute | 5.0
ALITOF_Xh_TotalVolAS |  | Exhaust exhausted total volume |  | 0 | 100000 | [12 empty] | m3 | ####.# | AnalogStatus | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Xh_RTXMFC5002AS |  | Exhaust XMFC5002 running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Gs_RefAtmPrSXAS |  | GasSystem reference (filtred) Surface atm pressure |  | 900 | 1100 | [12 empty] | mbar | ##.# | AnalogStatus | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute | 0.2
ALITOF_Gs_RefAtmPrUXAS |  | GasSystem reference (filtred) Underground atm pressure |  | 900 | 1100 | [12 empty] | mbar | ##.# | AnalogStatus | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details | pressure |  | Deadband AND Time | 1800.0 | Absolute | 0.2 |  |  |  | Absolute | 0.2
ALITOF_Gs_GasLossRateAS |  | GasSystem gas loss rate |  | -10000 | 10000 | [12 empty] | l/h | ##.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Time | 60.0 | [5 empty] | Absolute | 0.2
ALITOF_Gs_CurGasLossAS |  | GasSystem current total gas loss |  | -10000 | 10000 | [12 empty] | l/h | ##.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 200.0 |  |  |  | Absolute | 200.0
ALITOF_Gs_IntGasLossAS |  | GasSystem integrated gas loss |  | -1000000 | 1000000 | [12 empty] | m3 | ####.# | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Time | 60.0 | [5 empty] | Absolute | 0.2
ALITOF_Gs_SpareAS1 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS2 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS3 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS4 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS5 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS6 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS7 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS8 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS9 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS10 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS11 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS12 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS13 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS14 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS15 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS16 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS17 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS18 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS19 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Gs_SpareAS20 |  | GasSystem Spare AS |  | 0 | 100 | [13 empty] | #.## | AnalogStatus |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | 60 | [5 empty] | No | 1e-05
ALITOF_Mx_FillTotVolAS |  | Mixer fill volume |  | 0 | 100000 | [12 empty] | m3 | ####.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 0.1
ALITOF_Mx_L1CompRatioAS |  | Mixer L1 ratio |  | 0 | 100 | [12 empty] | % | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.05
ALITOF_Mx_L2CompRatioAS |  | Mixer L2 ratio |  | 0 | 100 | [12 empty] | % | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Mx_L3CompRatioAS |  | Mixer L3 ratio |  | 0 | 100 | [12 empty] | % | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Mx_L1CompRDAS |  | Mixer L1 comp. ratio dev. |  | 0 | 100 | [12 empty] | % | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 1.0
ALITOF_Mx_L2CompRDAS |  | Mixer L2 comp. ratio dev. |  | 0 | 100 | [12 empty] | % | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 1.0
ALITOF_Mx_L3CompRDAS |  | Mixer L3 comp. ratio dev. |  | 0 | 100 | [12 empty] | % | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Absolute | 1.0
ALITOF_Mx_L1FlowAS |  | Mixer L1 current flow |  | 0 | 528 | [12 empty] | l/h | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | No | [6 empty] | Absolute | 0.528
ALITOF_Mx_L2FlowAS |  | Mixer L2 current flow |  | 0 | 258 | [12 empty] | l/h | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | No | [6 empty] | Absolute | 0.01935
ALITOF_Mx_L3FlowAS |  | Mixer L3 current flow |  | 0 | 258 | [12 empty] | l/h | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | No | [6 empty] | Absolute | 0.01935
ALITOF_Mx_L1FlowDevAS |  | Mixer L1 flow deviation |  | 0 | 1000 | [12 empty] | l/h | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | No | [6 empty] | Absolute | 10.0
ALITOF_Mx_L2FlowDevAS |  | Mixer L2 flow deviation |  | 0 | 1000 | [12 empty] | l/h | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | No | [6 empty] | Absolute | 10.0
ALITOF_Mx_L3FlowDevAS |  | Mixer L3 flow deviation |  | 0 | 1000 | [12 empty] | l/h | ##.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | No | [6 empty] | Absolute | 10.0
ALITOF_Mx_PurgeTotVolAS |  | Mixer purge volume |  | 0 | 100000 | [12 empty] | m3 | ####.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 0.1
ALITOF_Mx_RTXMFC1206AS |  | Mixer low flow L2 MFC running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_RTXMFC1306AS |  | Mixer low flow L3 MFC running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_RTXMFC1209AS |  | Mixer high flow L2 MFC running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_RTXMFC1309AS |  | Mixer high flow L3 MFC running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_RTXMFC1106AS |  | Mixer low flow L1 MFC running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_RTXMFC1109AS |  | Mixer high flow L1 MFC running time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_TotalFlowAS |  | Mixer total flow |  | 0 | 1044 | [12 empty] | l/h | ###.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details | flow |  | Deadband AND Time | 1800.0 | Absolute | 1.0 |  |  |  | Absolute | 0.5
ALITOF_Mx_TotalVolAS |  | Mixer total supplied gas volume |  | 0 | 100000 | [12 empty] | m3 | ####.# | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1
ALITOF_Mx_CN1206Kc |  | CN1206 – Kc for XMFC1206 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.## | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1306Kc |  | CN1306 – Kc for XMFC1306 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.## | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1206Ti |  | CN1206 – Ti for XMFC1206 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1306Ti |  | CN1306 – Ti for XMFC1306 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1206Td |  | CN1206 – Td for XMFC1206 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1306Td |  | CN1306 – Td for XMFC1306 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1206Tds |  | CN1206 – Tds for XMFC1206 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1306Tds |  | CN1306 – Tds for XMFC1306 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1209Kc |  | CN1209 – Kc for XMFC1209 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.## | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1309Kc |  | CN1309 – Kc for XMFC1309 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.## | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1209Ti |  | CN1209 – Ti for XMFC1209 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1309Ti |  | CN1309 – Ti for XMFC1309 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1209Td |  | CN1209 – Td for XMFC1209 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1309Td |  | CN1309 – Td for XMFC1309 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1209Tds |  | CN1209 – Tds for XMFC1209 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Mx_CN1309Tds |  | CN1309 – Tds for XMFC1309 flow regulation |  | 0.0 | 90000.0 | [13 empty] | #.### | AnalogStatus | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800 | Absolute | 1.8000002 |  |  |  | Absolute | 0.0001
ALITOF_Pp_PressureRDAS |  | pressure regulation deviation |  | 0 | 100 | [12 empty] | - | #.# | AnalogStatus |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 10.0
ALITOF_Pp_RunTime1AS |  | 1 running delta time (totalizer time) |  | 0 | 90000 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.09
ALITOF_Pp_RunTime2AS |  | 2 running delta time (totalizer time) |  | 0.0 | 90000.0 | [12 empty] | h | #.# | AnalogStatus | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 1.0E-4
ALITOF_Pp_CN4003Kc |  | CN4003 – Kc for Pump Pressure regulation |  | 0.0 | 100.0 | [13 empty] | #.## | AnalogStatus |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 10.0
ALITOF_Pp_CN4003Ti |  | CN4003 – Ti for Pump Pressure regulation |  | 0.0 | 100.0 | [13 empty] | #.### | AnalogStatus |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 10.0
ALITOF_Pp_CN4003Td |  | CN4003 – Td for Pump Pressure regulation |  | 0.0 | 100.0 | [13 empty] | #.### | AnalogStatus |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 10.0
ALITOF_Pp_CN4003Tds |  | CN4003 – Tds for Pump Pressure regulation |  | 0.0 | 100.0 | [13 empty] | #.### | AnalogStatus |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | No | [6 empty] | Relative | 10.0
ALITOF_P1_CANmOfReg |  | Purifier1 col A nber of regeneration cycles |  | 0 | 100 | [12 empty] | - | ### | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | No
ALITOF_P1_CBNmOfReg |  | Purifier1 col B nber of regeneration cycles |  | 0 | 100 | [12 empty] | - | ### | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | No
ALITOF_P1_CANmRApOffset |  | Column A run total volume Applied offset |  | 0.0 | 10000.0 | [12 empty] | m3 | #.# | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison AND Time | 1800.0 | [5 empty] | Old/New
ALITOF_P1_CBNmRApOffset |  | Column B run total volume Applied offset |  | 0.0 | 10000.0 | [12 empty] | m3 | #.# | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison AND Time | 1800.0 | [5 empty] | Old/New
ALITOF_P1_CARApVOffset |  | Column A run total volume offset |  | 0.0 | 10000.0 | [12 empty] | m3 | #.# | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison AND Time | 1800.0 | [5 empty] | Old/New
ALITOF_P1_CBRApVOffset |  | Column B run total volume offset |  | 0.0 | 10000.0 | [12 empty] | m3 | #.# | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Old/New Comparison AND Time | 1800.0 | [5 empty] | Old/New
ALITOF_P1_CARunVol |  | Purifier1 col A run volume totalizer |  | 0 | 10000 | [12 empty] | m3 | ####.# | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.0 |  |  |  | Absolute | 1.0
ALITOF_P1_CBRunVol |  | Purifier1 col B run volume totalizer |  | 0 | 10000 | [12 empty] | m3 | ####.# | AnalogStatus | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | TOF_Details | TOF_Details |  |  | Deadband AND Time | 1800.0 | Absolute | 1.0 |  |  |  | Absolute | 1.0

## Local
Name | Local
Package | CPC
Object Type Family | FieldObjectFamily
Description | Local Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  | FEDeviceEnvironmentInputs |  | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | [9 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Remarks | Full/Empty Animation | Position Alarm | Feedback On | Feedback Off | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Message | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## OnOff
Name | OnOff
Package | CPC
Object Type Family | FieldObjectFamily
Description | OnOff Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [5 empty] | FEDeviceEnvironmentInputs |  |  |  |  | FEDeviceOutputs |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | [20 empty] | SCADADeviceClassificationTags | [7 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | Full/Empty Animation | Manual Restart after Full Stop | Constant Time Pulse | Warning Time Delay (s) | Pulse Duration (s) | Feedback On | Feedback Off | Local Drive | Local On | Local Off | Process Output | Process Output Off | Widget Type | Label On | Label Off | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template
ALITOF_Di_YC60991 |  | Distribution run state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_XLED60991 |  | OnOffSquare |  |  | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | Y¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\YC60991.py
ALITOF_Di_YC60992 |  | Distribution not ready state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_XLED60992 |  | OnOffSquare |  |  | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | Y¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\YC60992.py
ALITOF_Di_YC60993 |  | Distribution com. Purge state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_XLED60993 |  | OnOffSquare |  |  | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | Y¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\YC60993.py
ALITOF_Di_YC60994 |  | Distribution stop state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_XLED60994 |  | OnOffSquare |  |  | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | Y¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\YC60994.py
ALITOF_Di_YC60995 |  | Distribution process ctrl alarm LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_XLED60995 |  | OnOffSquare |  |  | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | Y¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\YC60995.py
ALITOF_Di_YC60996 |  | Distribution interlock LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_XLED60996 |  | OnOffSquare |  |  | ALITOF/ALITOF_DistributionRackFrontPanel.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | Y¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\YC60996.py
ALITOF_Di_SafeChain61Ak |  | Distribution rack 61 safety chain button |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\SafeChainiAk.py
ALITOF_Di_SafeChain62Ak |  | Distribution rack 62 safety chain button |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\SafeChainiAk.py
ALITOF_Di_YV6123 |  | Distribution rack 61 input valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6123 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | 0¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi23.py
ALITOF_Di_YV6223 |  | Distribution rack 62 input valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6223 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | 0¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi23.py
ALITOF_Di_YV6127 |  | Distribution rack 61 output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6127 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi27.py
ALITOF_Di_YV6227 |  | Distribution rack 62 output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6227 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi27.py
ALITOF_Di_YV6171 |  | Distribution rack 61 safety backup valve |  | On/Open | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6171 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi71.py
ALITOF_Di_YV6271 |  | Distribution rack 62 safety backup valve |  | On/Open | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6271 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi71.py
ALITOF_Di_YV6172 |  | Distribution rack 61 output selection valve |  | On/Open | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6172 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi72.py
ALITOF_Di_YV6272 |  | Distribution rack 62 output selection valve |  | On/Open | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Di_YY6272 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\YVi72.py
ALITOF_Di_FCRackSpeedOO |  | Distribution rack speed cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [8 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Di_DiPCO
ALITOF_Xh_ResetVolume |  | Exhaust volume reset |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\ResetVolume.py
ALITOF_Xh_YC5099_1 |  | Exhaust run state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Xh_XLED5099_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\YC5099_1.py
ALITOF_Xh_YC5099_2 |  | Exhaust venting state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Xh_XLED5099_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\YC5099_2.py
ALITOF_Xh_YC5099_3 |  | Exhaust stop state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Xh_XLED5099_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\YC5099_3.py
ALITOF_Xh_YC5099_4 |  | Exhaust process controla alarm LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Xh_XLED5099_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\YC5099_4.py
ALITOF_Xh_YC5099_5 |  | Exhaust interlock LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Xh_XLED5099_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_ExhaustRackFrontPanel.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\YC5099_5.py
ALITOF_Xh_YIC5003 |  | Exhaust selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 |  | ALITOF_Xh_ZSH5003 | ALITOF_Xh_ZSL5003 |  |  |  | ALITOF_Xh_YYH5003 | ALITOF_Xh_YYL5003 | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Exhaust.xml | ALITOF/ALITOF_Xh_YIC5003_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\YIC5003.py
ALITOF_Xh_ResXMFC5002 |  | ExhaustXMFC5002 reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Xh_XhPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\ResetTimer.py
ALITOF_Gs_YC0505 |  | GasSystem Gas System ready for physics (DSS) |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_GSY0505 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystem.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | 2¦1 | 0¦1 | 1¦0 | 1¦1 | 0¦1 | 0¦0 | 0¦0 | 0¦ | 0¦0 | 0¦ | GasSystem\GsPCO\YC0505.py
ALITOF_Gs_YC0506 |  | GasSystem surface 24v elec MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0506 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0506.py
ALITOF_Gs_YC0507 |  | GasSystem surface 24v valves MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0507 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0507.py
ALITOF_Gs_YC0599_1 |  | GasSystem surface control rack RUN state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_1.py
ALITOF_Gs_YC0599_10 |  | GasSystem surface control rack PLC canbus OK LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_10 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_10.py
ALITOF_Gs_YC0599_11 |  | GasSystem surface control rack PLC ioErr LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_11 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_11.py
ALITOF_Gs_YC0599_12 |  | GasSystem surface control rack PLC ioSim LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_12 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_12.py
ALITOF_Gs_YC0599_13 |  | GasSystem surface PSU fault LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_13 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_13.py
ALITOF_Gs_YC0599_15 |  | GasSystem surface WebMas running LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0599_15 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_15.py
ALITOF_Gs_YC0599_17 |  | GasSystem surface AC MCB trip LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_17 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_17.py
ALITOF_Gs_YC0599_18 |  | GasSystem surface 24v MCB trip LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_18 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_18.py
ALITOF_Gs_YC0599_2 |  | GasSystem surface control rack FILL state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_2.py
ALITOF_Gs_YC0599_20 |  | GasSystem surface Gas System ready for physics status (DSS) LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0599_20 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_20.py
ALITOF_Gs_YC0599_3 |  | GasSystem surface control rack PURGE state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_3.py
ALITOF_Gs_YC0599_4 |  | GasSystem surface control rack RECUPERATION state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_4.py
ALITOF_Gs_YC0599_5 |  | GasSystem surface control rack STOP state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_5.py
ALITOF_Gs_YC0599_6 |  | GasSystem surface control rack process alarms state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_6.py
ALITOF_Gs_YC0599_7 |  | GasSystem surface control rack interlocks LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_7 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_7.py
ALITOF_Gs_YC0599_8 |  | GasSystem surface control rack PLC running LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_8 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_8.py
ALITOF_Gs_YC0599_9 |  | GasSystem surface control rack PLC Profibus OK LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0599_9 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0599_9.py
ALITOF_Gs_YC0606 |  | GasSystem underground 24v elec MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0606 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0606.py
ALITOF_Gs_YC0607 |  | GasSystem underground 24v valves MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0607 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0607.py
ALITOF_Gs_YC0608 |  | GasSystem underground ELMB VA MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0608 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0608.py
ALITOF_Gs_YC0609 |  | GasSystem underground ELMB VC MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0609 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0609.py
ALITOF_Gs_YC0610 |  | GasSystem underground ELMB VD MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 1 | [5 empty] | ALITOF_Gs_XRES0610 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0610.py
ALITOF_Gs_YC0699_1 |  | GasSystem underground control rack RUN state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_1.py
ALITOF_Gs_YC0699_10 |  | GasSystem underground control rack PLC canbus OK LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_10 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_10.py
ALITOF_Gs_YC0699_11 |  | GasSystem underground control rack PLC ioErr LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_11 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_11.py
ALITOF_Gs_YC0699_12 |  | GasSystem underground control rack PLC ioSim LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_12 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_12.py
ALITOF_Gs_YC0699_13 |  | GasSystem underground PSU fault LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_13 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_13.py
ALITOF_Gs_YC0699_14 |  | GasSystem underground ELMB PSU fault LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_14 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_14.py
ALITOF_Gs_YC0699_15 |  | GasSystem underground WebMas running LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_15 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_15.py
ALITOF_Gs_YC0699_17 |  | GasSystem underground AC MCB trip LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_17 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_17.py
ALITOF_Gs_YC0699_18 |  | GasSystem underground 24v MCB trip LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_18 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_18.py
ALITOF_Gs_YC0699_19 |  | GasSystem underground ELMB MCB trip LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_19 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | 2¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_19.py
ALITOF_Gs_YC0699_2 |  | GasSystem underground control rack RUN state LEDcontrol rack FILL state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_2.py
ALITOF_Gs_YC0699_20 |  | GasSystem underground Gas System ready for physics status (DSS) LED |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Gs_XLED0699_20 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_20.py
ALITOF_Gs_YC0699_3 |  | GasSystem underground control rack PURGE state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_3.py
ALITOF_Gs_YC0699_4 |  | GasSystem underground control rack RECUPERATION state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_4.py
ALITOF_Gs_YC0699_5 |  | GasSystem underground control rack STOP state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_5.py
ALITOF_Gs_YC0699_6 |  | GasSystem underground control rack process alarms state LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_6.py
ALITOF_Gs_YC0699_7 |  | GasSystem underground control rack interlocks LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_7 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_7.py
ALITOF_Gs_YC0699_8 |  | GasSystem underground control rack PLC running LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_8 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_8.py
ALITOF_Gs_YC0699_9 |  | GasSystem underground control rack PLC Profibus OK LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Gs_XLED0699_9 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\YC0699_9.py
ALITOF_Gs_ELMBURst |  | GasSystem underground ELMB Global reset MCB reset cmd |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 30 | [5 empty] | ALITOF_Gs_XRES0608 |  | OnOffSquare |  |  | ALITOF/ALITOF_GasSystemRackFrontPanel.xml |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | GasSystem\GsPCO\ELMBURst.py
ALITOF_Gs_SpareOnOff1 |  | GasSystem Spare OnOff |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [8 empty] | OnOffSquare | [5 empty] | FALSE | TOF_Details | TOF_Details | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareOnOff2 |  | GasSystem Spare OnOff |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [8 empty] | OnOffSquare | [5 empty] | FALSE | TOF_Details | TOF_Details | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareOnOff3 |  | GasSystem Spare OnOff |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [8 empty] | OnOffSquare | [5 empty] | FALSE | TOF_Details | TOF_Details | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareOnOff4 |  | GasSystem Spare OnOff |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [8 empty] | OnOffSquare | [5 empty] | FALSE | TOF_Details | TOF_Details | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareOnOff5 |  | GasSystem Spare OnOff |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [8 empty] | OnOffSquare | [5 empty] | FALSE | TOF_Details | TOF_Details | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Mx_ResetVolume |  | Mixer reset volume totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\ResetVolume.py
ALITOF_Mx_ResXMFC1206 |  | Mixer low flow L2 MFC reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Mixer\MxPCO\ResetTimer.py
ALITOF_Mx_ResXMFC1306 |  | Mixer low flow L3 MFC reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Mixer\MxPCO\ResetTimer.py
ALITOF_Mx_ResXMFC1209 |  | Mixer high flow H2 MFC reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Mixer\MxPCO\ResetTimer.py
ALITOF_Mx_ResXMFC1309 |  | Mixer high flow H3 MFC reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Mixer\MxPCO\ResetTimer.py
ALITOF_Mx_ResXMFC1106 |  | Mixer low flow L1 MFC reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Mixer\MxPCO\ResetTimer.py
ALITOF_Mx_ResXMFC1109 |  | Mixer high flow H1 MFC reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Mixer\MxPCO\ResetTimer.py
ALITOF_Mx_YC1105 |  | Mixer L1 LF selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1105 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1105_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxL1PCO |  | 1¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxLiPCO\YC1i05.py
ALITOF_Mx_YC1205 |  | Mixer L2 LF selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1205 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1205_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxL2PCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxLiPCO\YC1i05.py
ALITOF_Mx_YC1305 |  | Mixer L3 LF selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1305 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1305_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxL3PCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxLiPCO\YC1i05.py
ALITOF_Mx_YC1108 |  | Mixer L1 HF selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1108 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1108_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxL1PCO |  | 1¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxLiPCO\YC1i08.py
ALITOF_Mx_YC1208 |  | Mixer L2 HF selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1208 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1208_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxL2PCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxLiPCO\YC1i08.py
ALITOF_Mx_YC1308 |  | Mixer L3 HF selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1308 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1308_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxL3PCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxLiPCO\YC1i08.py
ALITOF_Mx_YC1004 |  | Mixer constant flow sel. valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1004 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1004_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1004.py
ALITOF_Mx_YC1006 |  | Mixer fill pressure reg. sel. valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1006 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1006_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1006.py
ALITOF_Mx_YC1008 |  | Mixer bypass sel. valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_YV1008 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_YC1008_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | ¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1008.py
ALITOF_Mx_YC1099_1 |  | Mixer run LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_1.py
ALITOF_Mx_YC1099_2 |  | Mixer fill LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_2.py
ALITOF_Mx_YC1099_3 |  | Mixer purge LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_3.py
ALITOF_Mx_YC1099_4 |  | Mixer direct LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_4.py
ALITOF_Mx_YC1099_5 |  | Mixer stop LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_5.py
ALITOF_Mx_YC1099_6 |  | Mixer anomalies LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_6.py
ALITOF_Mx_YC1099_7 |  | Mixer interlock LED |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Mx_XLED1099_7 |  | OnOffSquare |  |  | ALITOF/ALITOF_MixerRackFrontPanel.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | Y¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦ | Mixer\MxPCO\YC1099_7.py
ALITOF_Pp_ResetTimer1 |  | pump device 1 reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\ResetTimeri.py
ALITOF_Pp_ResetTimer2 |  | pump device 2 reset running hours totalizer |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\ResetTimeri.py
ALITOF_Pp_YC4099_1 |  | run state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_XLED4099_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4099_1.py
ALITOF_Pp_YC4099_3 |  | starting state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_XLED4099_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4099_3.py
ALITOF_Pp_YC4099_4 |  | stop state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_XLED4099_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4099_4.py
ALITOF_Pp_YC4099_5 |  | process control alarm led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_XLED4099_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4099_5.py
ALITOF_Pp_YC4099_6 |  | interlock led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_XLED4099_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_PumpRackFrontPanel.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4099_6.py
ALITOF_Pp_YL4101 |  | pump device 1 status led |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Pp_XLED4101 |  | OnOffSquare |  |  |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | ¦2 | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YL4i01.py
ALITOF_Pp_YL4201 |  | pump device 2 status led |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Pp_XLED4201 |  | OnOffSquare |  |  |  |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | ¦2 | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YL4i01.py
ALITOF_Pp_PUMP4101 |  | on/off pump device:1 |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Pp_YC4101 |  | OnOffPumpHorizontalRight |  |  | ALITOF/ALITOF_Pump.xml | ALITOF/ALITOF_Pp_PUMP4101_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | ¦ | ¦ | ¦ | ¦ | ¦1 | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\Pump4i01.py
ALITOF_Pp_PUMP4201 |  | on/off pump device:2 |  | Off/Close | Full/Half/Empty | FALSE |  | 0 | [6 empty] | ALITOF_Pp_YC4201 |  | OnOffPumpHorizontalRight |  |  | ALITOF/ALITOF_Pump.xml | ALITOF/ALITOF_Pp_PUMP4201_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | ¦ | ¦ | ¦ | ¦ | ¦2 | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\Pump4i01.py
ALITOF_Pp_YC4002 |  | device bypass security valve |  | On/Open | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_YV4002 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Pump.xml | ALITOF/ALITOF_Pp_YC4002_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦2 | ¦ | ¦ | ¦7 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4002.py
ALITOF_Pp_YC4040 |  | output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_Pp_YY4040 |  | OnOffValveHorizontal |  |  | ALITOF/ALITOF_Pump.xml | ALITOF/ALITOF_Pp_YC4040_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_Pp_PpPCO |  | A¦ | ¦ | ¦ | ¦7 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\YC4040.py
ALITOF_P1_CANmOfRegRst |  | Purifier1 col A regeneration cycles reset |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦ | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\CiNmOfRegRst.py
ALITOF_P1_CBNmOfRegRst |  | Purifier1 col B regeneration cycles reset |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦ | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\CiNmOfRegRst.py
ALITOF_P1_CArunVolRst |  | Purifier1 col A volume reset |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦ | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\CiRunVolRst.py
ALITOF_P1_CBrunVolRst |  | Purifier1 col B volume reset |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | 2 | [7 empty] | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦ | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\CiRunVolRst.py
ALITOF_P1_Pump2005 |  | Purifier1 extraction pump |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YIC2005 |  | OnOffPumpHorizontalLeft |  |  | ALITOF/ALITOF_Purifier1.xml | ALITOF/ALITOF_P1_Pump2005_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | ¦ | ¦0 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\Pumpi005.py
ALITOF_P1_YC2199_1 |  | Purifier1 col A Run sequence state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_1.py
ALITOF_P1_YC2299_1 |  | Purifier1 col B Run sequence state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_1.py
ALITOF_P1_YC2199_2 |  | Purifier1 col A regeneration sequence led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_2.py
ALITOF_P1_YC2299_2 |  | Purifier1 col B regeneration sequence led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_2.py
ALITOF_P1_YC2199_3 |  | Purifier1 col A cool down state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_3.py
ALITOF_P1_YC2299_3 |  | Purifier1 col B cool down state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_3.py
ALITOF_P1_YC2199_4 |  | Purifier1 col A stand by state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_4.py
ALITOF_P1_YC2299_4 |  | Purifier1 col B stand by state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_4.py
ALITOF_P1_YC2199_5 |  | Purifier1 col A purge state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_5.py
ALITOF_P1_YC2299_5 |  | Purifier1 col B purge state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_5.py
ALITOF_P1_YC2199_6 |  | Purifier1 col A sopt state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_6.py
ALITOF_P1_YC2299_6 |  | Purifier1 col B sopt state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_6.py
ALITOF_P1_YC2199_8 |  | Purifier1 col A process control alarms led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_8 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_8.py
ALITOF_P1_YC2299_8 |  | Purifier1 col B process control alarms led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_8 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_8.py
ALITOF_P1_YC2199_9 |  | Purifier1 col A interlocks alarms |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2199_9 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_9.py
ALITOF_P1_YC2299_9 |  | Purifier1 col B interlocks alarms |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2299_9 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YCij99_9.py
ALITOF_P1_YC2099_1 |  | Purifier1 run state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_1 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_1.py
ALITOF_P1_YC2099_2 |  | Purifier1 single column A state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_2 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_2.py
ALITOF_P1_YC2099_3 |  | Purifier1 single column B state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_3 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_3.py
ALITOF_P1_YC2099_4 |  | Purifier1 double column state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_4 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_4.py
ALITOF_P1_YC2099_5 |  | Purifier1 free run state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_5 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_5.py
ALITOF_P1_YC2099_6 |  | Purifier1 stop state led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_6 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_6.py
ALITOF_P1_YC2099_8 |  | Purifier1 process control alarms led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_8 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_8.py
ALITOF_P1_YC2099_9 |  | Purifier1 interlocks led |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_XLED2099_9 |  | OnOffSquare |  |  | ALITOF/ALITOF_Purifier1RackFrontPanel.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦Y | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YCi099_9.py
ALITOF_P1_YV2103 |  | Purifier1 col A input valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 |  | ALITOF_P1_ZSH2103 | ALITOF_P1_ZSL2103 |  |  |  | ALITOF_P1_YY2103 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2103_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij03.py
ALITOF_P1_YV2203 |  | Purifier1 col B input valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 |  | ALITOF_P1_ZSH2203 | ALITOF_P1_ZSL2203 |  |  |  | ALITOF_P1_YY2203 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2203_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij03.py
ALITOF_P1_YV2104 |  | Purifier1 col A prepare for run/purge valve purge/regeneration output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2104 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2104_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij04.py
ALITOF_P1_YV2204 |  | Purifier1 col B prepare for run/purge valve purge/regeneration output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2204 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2204_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij04.py
ALITOF_P1_YV2105 |  | Purifier1 col A prepare for run/purge valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2105 |  | OnOff3WayValveVerticalLeftOnDown |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2105_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij05.py
ALITOF_P1_YV2205 |  | Purifier1 col B prepare for run/purge valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2205 |  | OnOff3WayValveVerticalLeftOnDown |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2205_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij05.py
ALITOF_P1_YV2106 |  | Purifier1 col A purge/regeneration input valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2106 |  | OnOff3WayValveVerticalLeftOnDown |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2106_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij06.py
ALITOF_P1_YV2206 |  | Purifier1 col B purge/regeneration input valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2206 |  | OnOff3WayValveVerticalLeftOnDown |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2206_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij06.py
ALITOF_P1_YV2107 |  | Purifier1 col A output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 |  | ALITOF_P1_ZSH2107 | ALITOF_P1_ZSL2107 |  |  |  | ALITOF_P1_YY2107 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2107_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij07.py
ALITOF_P1_YV2207 |  | Purifier1 col B output valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 |  | ALITOF_P1_ZSH2207 | ALITOF_P1_ZSL2207 |  |  |  | ALITOF_P1_YY2207 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2207_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij07.py
ALITOF_P1_YV2110 |  | Purifier1 col A purge valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2110 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2110_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij10.py
ALITOF_P1_YV2210 |  | Purifier1 col B purge valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2210 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2210_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij10.py
ALITOF_P1_YV2111 |  | Purifier1 col A regeneration valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2111 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnA.xml | ALITOF/ALITOF_P1_YV2111_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij11.py
ALITOF_P1_YV2211 |  | Purifier1 col B regeneration valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2211 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1ColumnB.xml | ALITOF/ALITOF_P1_YV2211_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\YVij11.py
ALITOF_P1_YV2001_1 |  | Purifier1 bypass valve |  | On/Open | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2001_1 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1.xml | ALITOF/ALITOF_P1_YV2001_1_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YVi001_1.py
ALITOF_P1_YV2001_2 |  | Purifier1 selection valve |  | Off/Close | Full/Half/Empty | FALSE |  | 1 | [6 empty] | ALITOF_P1_YY2001_2 |  | OnOffValveVertical |  |  | ALITOF/ALITOF_Purifier1.xml | ALITOF/ALITOF_P1_YV2001_2_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦ | ¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\YVi001_2.py

## Analog
Name | Analog
Package | CPC
Object Type Family | FieldObjectFamily
Description | Analog Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [7 empty] | FEDeviceManualRequests |  | FEDeviceEnvironmentInputs |  |  |  |  | FEDeviceOutputs | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [23 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | Manual Restart after Full Stop | Warning Time Delay (s) | Warning Deadband Value (Unit) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Manual Increase Step (Unit) | Manual Decrease Step (Unit) | Parameter Limit On/Open | Parameter Limit Off/Closed | Feedback Analog | Feedback On | Feedback Off | Hardware Analog Output | Local Drive | Process Output | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template
ALITOF_Di_PCV6126 |  | Distribution rack 61 pressure regulation valve |  | Off/Close | FALSE | 0 | 5.0 | 100 | 100 | 1 | 1 | 100 | 0 | ALITOF_Di_ZC6126F |  |  |  |  | ALITOF_Di_ZC6126 | % | ##.# | AnalogValveHorizontal | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  | ALITOF_Di_CN6126 | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1 | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\PCVi26.py
ALITOF_Di_PCV6226 |  | Distribution rack 62 pressure regulation valve |  | Off/Close | FALSE | 0 | 5.0 | 100 | 100 | 1 | 1 | 100 | 0 | ALITOF_Di_ZC6226F |  |  |  |  | ALITOF_Di_ZC6226 | % | ##.# | AnalogValveHorizontal | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  | ALITOF_Di_CN6226 | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1 | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiRackiPCO\PCVi26.py
ALITOF_Gs_SpareAnalog1 |  | Spare Analog |  | Off/Close | FALSE | 0 | 0.01 | 100 | 100 | 1 | 1 | 100 | 0 | [6 empty] | % | ##.# | AnalogValveHorizontal |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.1 |  |  |  | No | 0.05
ALITOF_Gs_SpareAnalog2 |  | Spare Analog |  | Off/Close | FALSE | 0 | 0.01 | 100 | 100 | 1 | 1 | 100 | 0 | [6 empty] | % | ##.# | AnalogValveHorizontal |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.1 |  |  |  | No | 0.05
ALITOF_Gs_SpareAnalog3 |  | Spare Analog |  | Off/Close | FALSE | 0 | 0.01 | 100 | 100 | 1 | 1 | 100 | 0 | [6 empty] | % | ##.# | AnalogValveHorizontal |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.1 |  |  |  | No | 0.05
ALITOF_Gs_SpareAnalog4 |  | Spare Analog |  | Off/Close | FALSE | 0 | 0.01 | 100 | 100 | 1 | 1 | 100 | 0 | [6 empty] | % | ##.# | AnalogValveHorizontal |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.1 |  |  |  | No | 0.05
ALITOF_Gs_SpareAnalog5 |  | Spare Analog |  | Off/Close | FALSE | 0 | 0.01 | 100 | 100 | 1 | 1 | 100 | 0 | [6 empty] | % | ##.# | AnalogValveHorizontal |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | 1800 | Absolute | 0.1 |  |  |  | No | 0.05
ALITOF_Pp_PV4003 |  | pressure control valve |  | Off/Close | FALSE | 0 | 5.0 | 10 | 10 | 1 | 1 | 95 | 0 | ALITOF_Pp_ZC4003F |  |  |  |  | ALITOF_Pp_ZC4003 | % | ##.# | AnalogValveHorizontal | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  | ALITOF_Pp_CN4003 | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.1 | ALITOF_Pp_PpPCO |  | ¦ | ¦ | ¦ | ¦ | False¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\PV4003.py
ALITOF_P1_TZ2101 |  | Purifier1 col A heater |  | Off/Close | FALSE | 0 | 5.0 | 100 | 100 | 1 | 1 | 100 | 0 | [5 empty] | ALITOF_P1_TZY2101 | % | ##.# | AnalogHeaterHorizontal | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | heater | ALITOF_P1_CNTZ2101 | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.05 | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\TZij01.py
ALITOF_P1_TZ2201 |  | Purifier1 col B heater |  | Off/Close | FALSE | 0 | 5.0 | 100 | 100 | 1 | 1 | 100 | 0 | [5 empty] | ALITOF_P1_TZY2201 | % | ##.# | AnalogHeaterHorizontal | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | heater | ALITOF_P1_CNTZ2201 | Deadband AND Time | 1800.0 | Absolute | 0.1 |  |  |  | Absolute | 0.05 | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\TZij01.py

## AnalogDigital
Name | AnalogDigital
Package | CPC
Object Type Family | FieldObjectFamily
Description | Analog Digital Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [14 empty] | FEDeviceManualRequests |  | FEDeviceEnvironmentInputs |  |  |  |  | FEDeviceOutputs |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [11 empty] | PWM Parameters | [19 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | PWM Mode | Outputs Maintained | Manual Restart after Full Stop | Range Min | Range Max | Warning Time Delay (s) | Warning Deadband Value (Unit) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Manual Increase Step (Unit) | Manual Decrease Step (Unit) | Time Period (s) | Max Deviation | Minimum Duration (s) | Parameter Limit On/Open | Parameter Limit Off/Closed | Feedback Analog | Feedback On | Feedback Off | Hardware Analog Output | Local Drive | Output On | Output Off | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## AnaDO
Name | AnaDO
Package | CPC
Object Type Family | FieldObjectFamily
Description | Unicos TCT type for the ANADO Object Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [7 empty] | FEDeviceManualRequests |  | FEDeviceEnvironmentInputs | [5 empty] | FEDeviceOutputs |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [25 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | Manual Restart after Full Stop | Warning Time Delay (s) | Warning Deadband Value (Unit) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Manual Increase Step (Unit) | Manual Decrease Step (Unit) | Parameter Limit On/Open | Parameter Limit Off/Closed | Feedback Analog | Feedback On | Local Drive | Hardware Analog Output | Local On | Local Off | Analog Process Output | Digital Process Output | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template
ALITOF_Gs_Spare1 |  | Spare AnaDO |  | Off/Close | FALSE | 1 | 2.0 | 5 | 100 | 0.1 | 0.1 | 90.0 | 10.0 | [8 empty] | % | #.# | AnaDOSquare |  |  |  |  | TOF_Details | TOF_Details | pump |  | No |  | Absolute |  |  |  |  | No | 0.1 |  |  | ¦
ALITOF_Gs_Spare2 |  | Spare AnaDO |  | Off/Close | FALSE | 1 | 2.0 | 5 | 100 | 0.1 | 0.1 | 90.0 | 10.0 | [8 empty] | % | #.# | AnaDOSquare |  |  |  |  | TOF_Details | TOF_Details | pump |  | No |  | Absolute |  |  |  |  | No | 0.1 |  |  | ¦

## MassFlowController
Name | MassFlowController
Package | CPC
Object Type Family | FieldObjectFamily
Description | Mass Flow Controller Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [15 empty] | FEDeviceOutputs | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [12 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [11 empty] | SCADADriverDataSmoothing |  |  |  | LogicDeviceDefinitions
[5 empty] | ParReg | [17 empty] | FEChannel | [13 empty] | CurveName |  |  | Flow |  | Calibration |  | Totalizer |  |  |  | SCADADeviceClassificationTags |  |  | Modes | Flow |  |  |  | Totalizer | [6 empty] | Flow |  | Totalizer |  |  |  | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Electrical Diagram | Remarks | Fail-Safe | Feedback Off | Inhibit Totalizer cmd | Convert ratio to Unit/time | Noise Filter | Manual Restart after Full Stop | Warning Time Delay (s) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Flow Conversion | Volume Conversion | CC0 Max Flow (Unit/time) | CC1 Max Flow (Unit/time) | CC2 Max Flow (Unit/time) | Deadband (%) | Filtering Time (s) | Valve Order | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Widget Type | Synoptic | Diagnostic | WWW Link | CC0 | CC1 | CC2 | Unit | Format | Unit | Gas Name | Unit | Format | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template
ALITOF_Xh_XMFC5002 |  | Exhaust mass flow controller |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 120.0 | 120.0 |  | 1.0 |  | ALITOF_Xh_YIC5003 | 206 | Mx80_02_PXM_XMFC5002 |  |  |  | 0.0 | ALITOF_Xh_NodeXMFC5002 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | Process | Purge |  | l/h | ###.# | l/m | Process | l | ####.# | FALSE | TOF_Details | TOF_Details |  | ALITOF_Xh_CN5002 | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 1.5 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Xh_XhPCO |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\XMFC5002.py
ALITOF_Gs_SpareMFC1 |  | Spare MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 1234.56 | 1234.56 | 1234.56 | 1.0 |  |  | 0 | [10 empty] | MassFlowController |  |  |  | Air |  |  | l/h | ##.# | l/m | Air | l | ####.# | FALSE | TOF_Details | TOF_Details |  |  | No | No |  | Absolute |  | No | 0 | [5 empty] | No | 0.0 | Relative | 10.0 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareMFC2 |  | Spare MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 1234.56 | 1234.56 | 1234.56 | 1.0 |  |  | 0 | [10 empty] | MassFlowController |  |  |  | Air |  |  | l/h | ##.# | l/m | Air | l | ####.# | FALSE | TOF_Details | TOF_Details |  |  | No | No |  | Absolute |  | No | 0 | [5 empty] | No | 0.0 | Relative | 10.0 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareMFC3 |  | Spare MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 1234.56 | 1234.56 | 1234.56 | 1.0 |  |  | 0 | [10 empty] | MassFlowController |  |  |  | Air |  |  | l/h | ##.# | l/m | Air | l | ####.# | FALSE | TOF_Details | TOF_Details |  |  | No | No |  | Absolute |  | No | 0 | [5 empty] | No | 0.0 | Relative | 10.0 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Mx_XMFC1206 |  | Mixer low flow L2 MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 18.0 |  |  | 1.0 |  | ALITOF_Mx_YC1205 | 206 | Mx80_02_PXM_XMFC1206 |  |  |  | 10.0 | ALITOF_Mx_NodeXMFC1206 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_XMFC1206_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | i-C4H10 | i-C4H10 |  | l/h | ##.# | l/m | i-C4H10 | l | #.### | FALSE | TOF_Details | TOF_Details |  | ALITOF_Mx_CN1206 | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 0.5 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Mx_MxL2PCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦ | Mixer\MxLiPCO\XMFC1i06.py
ALITOF_Mx_XMFC1306 |  | Mixer low flow L3 MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 18.0 |  |  | 1.0 |  | ALITOF_Mx_YC1305 | 206 | Mx80_02_PXM_XMFC1306 |  |  |  | 0.0 | ALITOF_Mx_NodeXMFC1306 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_XMFC1306_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | SF6 | SF6 |  | l/h | ##.# | l/m | SF6 | l | #.### | FALSE | TOF_Details | TOF_Details |  | ALITOF_Mx_CN1306 | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 0.54 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Mx_MxL3PCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦ | Mixer\MxLiPCO\XMFC1i06.py
ALITOF_Mx_XMFC1209 |  | Mixer high flow L2 MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 240.0 |  |  | 1.0 |  | ALITOF_Mx_YC1208 | 206 | Mx80_02_PXM_XMFC1209 |  |  |  | 0.0 | ALITOF_Mx_NodeXMFC1209 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_XMFC1209_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | i-C4H10 | i-C4H10 |  | l/h | ###.# | l/m | i-C4H10 | l | #.### | FALSE | TOF_Details | TOF_Details |  | ALITOF_Mx_CN1209 | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 6.0 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Mx_MxL2PCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦ | Mixer\MxLiPCO\XMFC1i09.py
ALITOF_Mx_XMFC1309 |  | Mixer high flow L3 MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 240.0 |  |  | 1.0 |  | ALITOF_Mx_YC1308 | 206 | Mx80_02_PXM_XMFC1309 |  |  |  | 0.0 | ALITOF_Mx_NodeXMFC1309 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_XMFC1309_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | SF6 | SF6 |  | l/h | ###.# | l/m | SF6 | l | #.### | FALSE | TOF_Details | TOF_Details |  | ALITOF_Mx_CN1309 | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 5.0 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Mx_MxL3PCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦ | Mixer\MxLiPCO\XMFC1i09.py
ALITOF_Mx_XMFC1106 |  | Mixer low flow L1 MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 264.0 | 264.0 |  | 1.0 |  | ALITOF_Mx_YC1105 | 206 | Mx80_02_PXM_XMFC1106 |  |  |  | 0.0 | ALITOF_Mx_NodeXMFC1106 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_XMFC1106_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | C2H2F4 | i-C2H2F4 |  | l/h | ###.# | l/m | C2H2F4 | l | ####.# | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 5.0 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Mx_MxL1PCO |  | 1¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦ | Mixer\MxLiPCO\XMFC1i06.py
ALITOF_Mx_XMFC1109 |  | Mixer high flow L1 MFC |  |  | Off/Close | FALSE | FALSE | FALSE | TRUE | FALSE | 1.0 | 0.0 | 0.0 | 60.0 | 60.0 | 4380.0 | 4380.0 |  | 1.0 |  | ALITOF_Mx_YC1108 | 206 | Mx80_02_PXM_XMFC1109 |  |  |  | 10.0 | ALITOF_Mx_NodeXMFC1109 |  |  |  | PxmCtrl | MassFlowController | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_XMFC1109_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | C2H2F4 | i-C2H2F4 |  | l/h | ####.# | l/m | C2H2F4 | l | ####.# | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | Deadband AND Time | 1800.0 | Absolute | 40.0 | No | [6 empty] | No |  | Relative | 0.0 | ALITOF_Mx_MxL1PCO |  | 1¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦ | Mixer\MxLiPCO\XMFC1i09.py

## SteppingMotor
Name | SteppingMotor
Package | CPC
Object Type Family | FieldObjectFamily
Description | Unicos TCT type for the Stepping Motor Object Device
Version | $LastChangedRevision: 0001 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [11 empty] | FEDeviceEnvironmentInputs |  |  | FEDeviceOutputs |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [18 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Switches Configuration | Feedback | Manual Restart after Full Stop | Reference Position | Minimum Range | Maximum Range | Scale | Offset | Max Speed | Warning Time Delay (s) | Warning Deadband Value (Unit) | Deadband Trigger | Feedback Analog | ClockWise Limit | CounterClockWise Limit | ClockWise to Reference Switch | Simulated Reference Switch | Driver Enable | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## Controller
Name | Controller
Package | CPC
Object Type Family | ControlObjectFamily
Description | Controller Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [5 empty] | FEDeviceAutoRequests |  | FEDeviceEnvironmentInputs | FEDeviceOutputs | FEDeviceVariables | [8 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [10 empty] | SCADADriverDataSmoothing |  |  |  | LogicDeviceDefinitions
|  |  |  | Controller Parameters | [5 empty] | Default Setpoint Speed |  |  |  | Default PID Parameters | [14 empty] | SCADADeviceClassificationTags | [5 empty] | MV and SP Archiving |  |  |  | Output Archiving |  |  |  | MV and SP Smoothing |  | Output Smoothing |  |  |  | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Output Range Min | Output Range Max | MV Filter Time (s) | PID Cycle (s) | Scaling Method | RA | Increase Speed | Decrease Speed | Measured Value | Controlled Objects | Setpoint | Kc | Ti | Td | Tds | SP High Limit | SP Low Limit | Out High Limit | Out Low Limit | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Deadband Type | Deadband Value | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template
ALITOF_Di_CN6126 |  | Distribution rack 61 pressure regulator |  |  |  | 0.1 | 0.1 | Input Scaling | TRUE | 1 | 1 | ALITOF_Di_PT6126 | ALITOF_Di_PCV6126 |  | 0.5 | 2 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_DistribRack61.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.02 |  | 1800.0 |  | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Di_DiRack61PCO |  | 0¦ALI_TOF | 1¦62 | 61¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1¦0 | Distribution\DiRackiPCO\CNi26.py
ALITOF_Di_CN6226 |  | Distribution rack 62 pressure regulator |  |  |  | 0.1 | 0.1 | Input Scaling | TRUE | 1 | 1 | ALITOF_Di_PT6226 | ALITOF_Di_PCV6226 |  | 0.5 | 5 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_DistribRack62.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.02 |  | 1800.0 |  | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Di_DiRack62PCO |  | 0¦ALI_TOF | 1¦62 | 62¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1¦0 | Distribution\DiRackiPCO\CNi26.py
ALITOF_Xh_CN5002 |  | Exhaust software pressure controller |  |  |  | 0.1 | 0.1 | Input Scaling | TRUE | 1 | 1 | ALITOF_Xh_PT5005 | ALITOF_Xh_XMFC5002 |  | 0.5 | 2 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.07 |  | 1800.0 |  | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Xh_XhPCO |  | Y¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\CN5002.py
ALITOF_Gs_SpareCtrl1 |  | Spare Ctrl |  | 0 | 100 | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | [9 empty] | 100 | 0 | Controller |  |  |  | FALSE | TOF_Details | TOF_Details | [13 empty] | No | 0.05 | No | 0.05 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareCtrl2 |  | Spare Ctrl |  | 0 | 100 | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | [9 empty] | 100 | 0 | Controller |  |  |  | FALSE | TOF_Details | TOF_Details | [13 empty] | No | 0.05 | No | 0.05 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareCtrl3 |  | Spare Ctrl |  | 0 | 100 | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | [9 empty] | 100 | 0 | Controller |  |  |  | FALSE | TOF_Details | TOF_Details | [13 empty] | No | 0.05 | No | 0.05 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareCtrl4 |  | Spare Ctrl |  | 0 | 100 | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | [9 empty] | 100 | 0 | Controller |  |  |  | FALSE | TOF_Details | TOF_Details | [13 empty] | No | 0.05 | No | 0.05 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SpareCtrl5 |  | Spare Ctrl |  | 0 | 100 | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | [9 empty] | 100 | 0 | Controller |  |  |  | FALSE | TOF_Details | TOF_Details | [13 empty] | No | 0.05 | No | 0.05 |  |  | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Mx_CN1206 |  | Mixer L2 LF controller |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_Mx_L2CompRatioAS | ALITOF_Mx_XMFC1206 |  | 0.5 | 1 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.1 | Deadband AND Time | 1800.0 | Absolute | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Mx_MxL2PCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦0 | Mixer\MxLiPCO\CN1i06.py
ALITOF_Mx_CN1306 |  | Mixer L3 LF controller |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_Mx_L3CompRatioAS | ALITOF_Mx_XMFC1306 |  | 0.5 | 1 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.1 | Deadband AND Time | 1800.0 | Absolute | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Mx_MxL3PCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦0 | Mixer\MxLiPCO\CN1i06.py
ALITOF_Mx_CN1209 |  | Mixer L2 HF controller |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_Mx_L2CompRatioAS | ALITOF_Mx_XMFC1209 |  | 0.5 | 5 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.1 | Deadband AND Time | 1800.0 | Absolute | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Mx_MxL2PCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦0 | Mixer\MxLiPCO\CN1i09.py
ALITOF_Mx_CN1309 |  | Mixer L3 HF controller |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_Mx_L3CompRatioAS | ALITOF_Mx_XMFC1309 |  | 0.5 | 5 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.1 | Deadband AND Time | 1800.0 | Absolute | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Mx_MxL3PCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | ¦0 | Mixer\MxLiPCO\CN1i09.py
ALITOF_Pp_CN4003 |  | Pressure regulation PID |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_Pp_PT4004 | ALITOF_Pp_PV4003 |  | 3 | 10 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 0.1 |  | 1800.0 |  | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_Pp_PpPCO |  | A¦ | ¦ | ¦ | 0¦ | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\CN4003.py
ALITOF_P1_CNTZ2101 |  | Purifier1 col A heater PID |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_P1_TE2101_2 | ALITOF_P1_TZ2101 |  | 2 | 10 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 4.2 |  | 1800.0 |  | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_P1_P1CAPCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦0 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\CNTZij01.py
ALITOF_P1_CNTZ2201 |  | Purifier1 col B heater PID |  |  |  | 0.1 | 0.1 | Input Scaling | FALSE | 1 | 1 | ALITOF_P1_TE2201_2 | ALITOF_P1_TZ2201 |  | 2 | 10 | 0 | 0 |  |  |  |  | Controller | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [6 empty] | 1800.0 |  | 4.2 |  | 1800.0 |  | 1.5 | Absolute | 0.0 | Absolute | 0.5 | ALITOF_P1_P1CBPCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦0 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\CNTZij01.py

## ProcessControlObject
Name | ProcessControlObject
Package | CPC
Object Type Family | ControlObjectFamily
Description | Process Control Object Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [8 empty] | SCADADeviceGraphics |  |  |  |  | SCADADeviceFunctionals | [12 empty] | SCADADeviceDataArchiving |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | Option Mode Allowance Table | [14 empty] | Mode Label | [7 empty] | SCADADeviceClassificationTags | [7 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Manual Restart after Full Stop | Option Mode 1 Allowance | Option Mode 2 Allowance | Option Mode 3 Allowance | Option Mode 4 Allowance | Option Mode 5 Allowance | Option Mode 6 Allowance | Option Mode 7 Allowance | Option Mode 8 Allowance | Widget Type | Display Name | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Option Mode 1 Label | Option Mode 2 Label | Option Mode 3 Label | Option Mode 4 Label | Option Mode 5 Label | Option Mode 6 Label | Option Mode 7 Label | Option Mode 8 Label | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | IL User Template | CL User Template | BL User Template | INST User Template | GL User Template | TL User Template | SL User Template | CDOL User Template | DL User Template
ALITOF_Di_DiRack61PCO |  | Distribution rack 61 PCO |  | FALSE | 00000000 | 00000000 | 00000000 | [5 empty] | PCO | Rack61 | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | Run | ComPurge | IndPurge | [5 empty] | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | 1¦62 | 61¦18 | 0¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1¦0 | Distribution\DiRackiPCO\DiRackiPCO_IL.py | Distribution\DiRackiPCO\DiRackiPCO_CL.py |  |  | Distribution\DiRackiPCO\DiRackiPCO_GL.py | Distribution\DiRackiPCO\DiRackiPCO_TL.py | Distribution\DiRackiPCO\DiRackiPCO_SL.py |  | Distribution\DiPCO\DiRackiPCO.py
ALITOF_Di_DiRack62PCO |  | Distribution rack 62 PCO |  | FALSE | 00000000 | 00000000 | 00000000 | [5 empty] | PCO | Rack62 | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | Run | ComPurge | IndPurge | [5 empty] | TOF_Details | [5 empty] | ALITOF_Di_DiPCO |  | 0¦ALI_TOF | 1¦62 | 62¦18 | 0¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1¦0 | Distribution\DiRackiPCO\DiRackiPCO_IL.py | Distribution\DiRackiPCO\DiRackiPCO_CL.py |  |  | Distribution\DiRackiPCO\DiRackiPCO_GL.py | Distribution\DiRackiPCO\DiRackiPCO_TL.py | Distribution\DiRackiPCO\DiRackiPCO_SL.py |  | Distribution\DiPCO\DiRackiPCO.py
ALITOF_Di_DiPCO |  | Distribution PCO |  | FALSE | 00000000 | 00000000 | [6 empty] | PCO | Distribution | ALITOF/ALITOF_Distribution.xml |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | Run | ComPurge | [6 empty] | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | 0¦ALI_TOF | ¦62 | ¦36 | ¦0 | 0¦0 | 0¦1 | 0¦1 | 0¦1 | 1¦1 | 1¦1 | Distribution\DiPCO\DiPCO_IL.py | Distribution\DiPCO\DiPCO_CL.py |  |  | Distribution\DiPCO\DiPCO_GL.py | Distribution\DiPCO\DiPCO_TL.py | Distribution\DiPCO\DiPCO_SL.py |  | GasSystem\GsPCO\DiPCO.py
ALITOF_Xh_XhPCO |  | Exhaust PCO |  | FALSE | 01000000 | 10000000 | [6 empty] | PCO | Exhaust | ALITOF/ALITOF_Exhaust.xml |  | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | Run | Vent | [6 empty] | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | Y¦Y | ¦0 | 0¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | Exhaust\XhPCO\XhPCO_IL.py | Exhaust\XhPCO\XhPCO_CL.py |  |  | Exhaust\XhPCO\XhPCO_GL.py | Exhaust\XhPCO\XhPCO_TL.py | Exhaust\XhPCO\XhPCO_SL.py |  | GasSystem\GsPCO\XhPCO.py
ALITOF_Gs_GsPCO |  | GasSystem PCO |  | FALSE | 00000000 | 00100000 | 00000000 | 00000000 |  |  |  |  | PCO | TOF |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | Purge | Fill | Run | Recuperate |  |  |  |  | TOF_Global | [7 empty] | 2¦1 | 0¦1 | 1¦0 | 1¦1 | 0¦1 | 0¦0 | 0¦0 | 0¦ | 0¦0 | 0¦0¦1¦1¦1 | GasSystem\GsPCO\GsPCO_IL.py | GasSystem\GsPCO\GsPCO_CL.py |  |  | GasSystem\GsPCO\GsPCO_GL.py | GasSystem\GsPCO\GsPCO_TL.py | GasSystem\GsPCO\GsPCO_SL.py
ALITOF_Gs_SparePCO1 |  | Spare PCO |  | FALSE | [8 empty] | PCO |  |  |  |  | FALSE | TOF_Details | [8 empty] | TOF_Global | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Gs_SparePCO2 |  | Spare PCO |  | FALSE | [8 empty] | PCO |  |  |  |  | FALSE | TOF_Details | [8 empty] | TOF_Global | [7 empty] | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
ALITOF_Mx_MxPCO |  | Mixer PCO |  | FALSE | 10100000 | 01000000 | 00100000 | 00010000 |  |  |  |  | PCO | Mixer | ALITOF/ALITOF_Mixer.xml |  | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | Fill | Purge | Run | Direct |  |  |  |  | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | ¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦N | Mixer\MxPCO\MxPCO_IL.py | Mixer\MxPCO\MxPCO_CL.py |  |  | Mixer\MxPCO\MxPCO_GL.py | Mixer\MxPCO\MxPCO_TL.py | Mixer\MxPCO\MxPCO_SL.py |  | GasSystem\GsPCO\MxPCO.py
ALITOF_Mx_MxL1PCO |  | Mixer gas line 1 PCO |  | FALSE | 11000000 | 11000000 | [6 empty] | PCO | MixerLine1 | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_MxL1PCO_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | LowFlow | HighFlow | [6 empty] | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | 1¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦N | Mixer\MxLiPCO\MxLiPCO_IL.py | Mixer\MxLiPCO\MxLiPCO_CL.py |  |  | Mixer\MxLiPCO\MxLiPCO_GL.py | Mixer\MxLiPCO\MxLiPCO_TL.py | Mixer\MxLiPCO\MxLiPCO_SL.py |  | Mixer\MxPCO\MxLiPCO.py
ALITOF_Mx_MxL2PCO |  | Mixer gas line 2 PCO |  | FALSE | 11000000 | 11000000 | [6 empty] | PCO | MixerLine2 | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_MxL2PCO_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | LowFlow | HighFlow | [6 empty] | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | 2¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦N | Mixer\MxLiPCO\MxLiPCO_IL.py | Mixer\MxLiPCO\MxLiPCO_CL.py |  |  | Mixer\MxLiPCO\MxLiPCO_GL.py | Mixer\MxLiPCO\MxLiPCO_TL.py | Mixer\MxLiPCO\MxLiPCO_SL.py |  | Mixer\MxPCO\MxLiPCO.py
ALITOF_Mx_MxL3PCO |  | Mixer gas line 3 PCO |  | FALSE | 11000000 | 11000000 | [6 empty] | PCO | MixerLine3 | ALITOF/ALITOF_Mixer.xml | ALITOF/ALITOF_Mx_MxL3PCO_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | LowFlow | HighFlow | [6 empty] | TOF_Details | [5 empty] | ALITOF_Mx_MxPCO |  | 3¦3 | Y¦N | 0¦N | N¦N | N¦N | Y¦N | ¦ | ¦N | N¦N | N¦N | Mixer\MxLiPCO\MxLiPCO_IL.py | Mixer\MxLiPCO\MxLiPCO_CL.py |  |  | Mixer\MxLiPCO\MxLiPCO_GL.py | Mixer\MxLiPCO\MxLiPCO_TL.py | Mixer\MxLiPCO\MxLiPCO_SL.py |  | Mixer\MxPCO\MxLiPCO.py
ALITOF_Pp_PpPCO |  | pump PCO |  | FALSE | 10000000 | [7 empty] | PCO | Pump | ALITOF/ALITOF_Pump.xml |  | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | Run | [7 empty] | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | A¦2 | 1¦0 | 2¦0 | 0¦7 | 0¦ | 1¦0 | ¦ | ¦ | ¦ | ¦ | Pump\PpPCO\PpPCO_IL.py | Pump\PpPCO\PpPCO_CL.py |  |  | Pump\PpPCO\PpPCO_GL.py | Pump\PpPCO\PpPCO_TL.py | Pump\PpPCO\PpPCO_SL.py |  | GasSystem\GsPCO\PpPCO.py
ALITOF_P1_P1PCO |  | Purifier1 PCO |  | FALSE | 01111000 | 10111000 | 11011000 | 11101000 | 11110000 | 00000000 | 00000000 |  | PCO | Purifier1 | ALITOF/ALITOF_Purifier1.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | NominalRun | CA_Run | CB_Run | CACB_Run | FreeRun |  |  |  | TOF_Details | [5 empty] | ALITOF_Gs_GsPCO |  | 2¦ | ¦Pu | 1¦1 | 0¦0 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuPCO\PuPCO_IL.py | PurifierCo2Absorber\PuPCO\PuPCO_CL.py |  |  | PurifierCo2Absorber\PuPCO\PuPCO_GL.py |  |  |  | GasSystem\GsPCO\P1PCO.py
ALITOF_P1_P1CAPCO |  | Purifier1 col A PCO |  | FALSE | 01011000 | 00110000 | 00010000 | 11001000 | 11000000 | 00000000 | 00000000 |  | PCO | P1CA | ALITOF/ALITOF_Purifier1ColumnA.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | StandBy | RunPreparation | Run | Regeneration | CoolDown | Purge | Free |  | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦1 | CA¦Pu | 1¦1 | 0¦0 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\PuCiPCO_IL.py | PurifierCo2Absorber\PuCiPCO\PuCiPCO_CL.py |  |  | PurifierCo2Absorber\PuCiPCO\PuCiPCO_GL.py | PurifierCo2Absorber\PuCiPCO\PuCiPCO_TL.py | PurifierCo2Absorber\PuCiPCO\PuCiPCO_SL.py |  | PurifierCo2Absorber\\PuPCO\PuCAPCO.py
ALITOF_P1_P1CBPCO |  | Purifier1 col B PCO |  | FALSE | 01011000 | 00110000 | 00010000 | 11001000 | 11000000 | 00000000 | 00000000 |  | PCO | P1CB | ALITOF/ALITOF_Purifier1ColumnB.xml |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | StandBy | RunPreparation | Run | Regeneration | CoolDown | Purge | Free |  | TOF_Details | [5 empty] | ALITOF_P1_P1PCO |  | 2¦2 | CB¦Pu | 1¦1 | 0¦0 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | PurifierCo2Absorber\PuCiPCO\PuCiPCO_IL.py | PurifierCo2Absorber\PuCiPCO\PuCiPCO_CL.py |  |  | PurifierCo2Absorber\PuCiPCO\PuCiPCO_GL.py | PurifierCo2Absorber\PuCiPCO\PuCiPCO_TL.py | PurifierCo2Absorber\PuCiPCO\PuCiPCO_SL.py |  | PurifierCo2Absorber\\PuPCO\PuCBPCO.py

## DigitalAlarm
Name | DigitalAlarm
Package | CPC
Object Type Family | ControlObjectFamily
Description | Digital Alarm Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | FEDeviceAlarm |  |  | FEDeviceEnvironmentInputs | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  | LogicDeviceDefinitions
[15 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config | [5 empty] | CustomLogicParameters
Name | Expert Name | Description | Remarks | Alarm Delay (s) | Type | Multiple Types | Auto Acknowledge | Input | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Masked | Level | Message | Master | Fast Interlock Type | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_61IndPuAl |  | Rack 1 individually purges alarm |  | logic | SI |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Rack 61 has been individually purged, put the manual valve back to the appropriate position before starting. | ALITOF_Di_DiRack61PCO
ALITOF_Di_62IndPuAl |  | Rack 1 individually purges alarm |  | logic | SI |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Rack 62 has been individually purged, put the manual valve back to the appropriate position before starting. | ALITOF_Di_DiRack62PCO
ALITOF_Di_AlarmInMod |  | Di module alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some alarms in Di module. | ALITOF_Di_DiPCO
ALITOF_Di_AlarmInRack61 |  | Rack 61 alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some alarms in rack 61 | ALITOF_Di_DiRack61PCO
ALITOF_Di_AlarmInRack62 |  | Rack 62 alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some alarms in rack 62 | ALITOF_Di_DiRack62PCO
ALITOF_Di_AtmPrSenDA |  | PT0201 - Atmospheric pressure sensor alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | PT0201 - Atmospheric pressure sensor is faulty. | ALITOF_Di_DiPCO
ALITOF_Di_DeviceDA |  | Profibus devices alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some profibus devices can not be reached. | ALITOF_Di_DiPCO
ALITOF_Di_noRackInRunAl |  | Module - No relevant racks in Run alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | There is not any relevant racks in Run. | ALITOF_Di_DiPCO
ALITOF_Di_RNotInComPAl |  | Module - Relevant rack not in Common Purge alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one relevant rack is not in Common Purge. | ALITOF_Di_DiPCO
ALITOF_Di_RNotInRunAl |  | Module - Relevant rack not in Run alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one relevant rack is not in Run. | ALITOF_Di_DiPCO
ALITOF_Di_RNotInRunRAl |  | Module - Relevant rack not in Run/Ready alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one relevant rack is not in Run/Ready. | ALITOF_Di_DiPCO
ALITOF_Di_RNotInStopAl |  | Module - Relevant rack not in Stop alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one relevant rack is not in Stop. | ALITOF_Di_DiPCO
ALITOF_Di_PCOUnAckAlDA |  | Child to Parent Alarm/interlock UnAcknowledge propagation |  | 0 | AL |  | TRUE |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one alarm/interlock of the Parent and Child PCO is not acknowledged | ALITOF_Di_DiPCO
ALITOF_Di_61GasLossAlDA |  | At least one Channel of Rack 61 has a Loss Alarm |  | 0 | FS |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | With CriticGas ON , At least one Channel of Rack 1 has a Loss Alarm | ALITOF_Di_DiRack61PCO
ALITOF_Di_62GasLossAlDA |  | At least one Channel of Rack 62 has a Loss Alarm |  | 0 | FS |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | With CriticGas ON , At least one Channel of Rack 1 has a Loss Alarm | ALITOF_Di_DiRack62PCO
ALITOF_Di_61Ch1GLosAl |  | FExx02-06/1 - Rack 61 channel 1 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/1 - Gas loss in Rack 61 channel 1. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch2GLosAl |  | FExx02-06/2 - Rack 61 channel 2 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/2 - Gas loss in Rack 61 channel 2. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch3GLosAl |  | FExx02-06/3 - Rack 61 channel 3 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/3 - Gas loss in Rack 61 channel 3. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch4GLosAl |  | FExx02-06/4 - Rack 61 channel 4 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/4 - Gas loss in Rack 61 channel 4. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch5GLosAl |  | FExx02-06/5 - Rack 61 channel 5 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/5 - Gas loss in Rack 61 channel 5. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch6GLosAl |  | FExx02-06/6 - Rack 61 channel 6 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/6 - Gas loss in Rack 61 channel 6. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch7GLosAl |  | FExx02-06/7 - Rack 61 channel 7 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/7 - Gas loss in Rack 61 channel 7. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch8GLosAl |  | FExx02-06/8 - Rack 61 channel 8 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/8 - Gas loss in Rack 61 channel 8. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch9GLosAl |  | FExx02-06/9 - Rack 61 channel 9 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/9 - Gas loss in Rack 61 channel 9. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch10GLosAl |  | FExx02-06/10 - Rack 61 channel 10 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/10 - Gas loss in Rack 61 channel 10. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch11GLosAl |  | FExx02-06/11 - Rack 61 channel 11 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/11 - Gas loss in Rack 61 channel 11. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch12GLosAl |  | FExx02-06/12 - Rack 61 channel 12 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/12 - Gas loss in Rack 61 channel 12. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch13GLosAl |  | FExx02-06/13 - Rack 61 channel 13 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/13 - Gas loss in Rack 61 channel 13. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch14GLosAl |  | FExx02-06/14 - Rack 61 channel 14 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/14 - Gas loss in Rack 61 channel 14. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch15GLosAl |  | FExx02-06/15 - Rack 61 channel 15 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/15 - Gas loss in Rack 61 channel 15. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch16GLosAl |  | FExx02-06/16 - Rack 61 channel 16 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/16 - Gas loss in Rack 61 channel 16. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch17GLosAl |  | FExx02-06/17 - Rack 61 channel 17 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/17 - Gas loss in Rack 61 channel 17. | ALITOF_Di_DiRack61PCO
ALITOF_Di_61Ch18GLosAl |  | FExx02-06/18 - Rack 61 channel 18 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/18 - Gas loss in Rack 61 channel 18. | ALITOF_Di_DiRack61PCO
ALITOF_Di_62Ch1GLosAl |  | FExx02-06/1 - Rack 62 channel 1 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/1 - Gas loss in Rack 62 channel 1. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch2GLosAl |  | FExx02-06/2 - Rack 62 channel 2 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/2 - Gas loss in Rack 62 channel 2. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch3GLosAl |  | FExx02-06/3 - Rack 62 channel 3 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/3 - Gas loss in Rack 62 channel 3. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch4GLosAl |  | FExx02-06/4 - Rack 62 channel 4 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/4 - Gas loss in Rack 62 channel 4. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch5GLosAl |  | FExx02-06/5 - Rack 62 channel 5 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/5 - Gas loss in Rack 62 channel 5. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch6GLosAl |  | FExx02-06/6 - Rack 62 channel 6 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/6 - Gas loss in Rack 62 channel 6. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch7GLosAl |  | FExx02-06/7 - Rack 62 channel 7 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/7 - Gas loss in Rack 62 channel 7. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch8GLosAl |  | FExx02-06/8 - Rack 62 channel 8 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/8 - Gas loss in Rack 62 channel 8. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch9GLosAl |  | FExx02-06/9 - Rack 62 channel 9 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/9 - Gas loss in Rack 62 channel 9. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch10GLosAl |  | FExx02-06/10 - Rack 62 channel 10 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/10 - Gas loss in Rack 62 channel 10. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch11GLosAl |  | FExx02-06/11 - Rack 62 channel 11 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/11 - Gas loss in Rack 62 channel 11. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch12GLosAl |  | FExx02-06/12 - Rack 62 channel 12 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/12 - Gas loss in Rack 62 channel 12. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch13GLosAl |  | FExx02-06/13 - Rack 62 channel 13 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/13 - Gas loss in Rack 62 channel 13. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch14GLosAl |  | FExx02-06/14 - Rack 62 channel 14 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/14 - Gas loss in Rack 62 channel 14. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch15GLosAl |  | FExx02-06/15 - Rack 62 channel 15 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/15 - Gas loss in Rack 62 channel 15. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch16GLosAl |  | FExx02-06/16 - Rack 62 channel 16 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/16 - Gas loss in Rack 62 channel 16. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch17GLosAl |  | FExx02-06/17 - Rack 62 channel 17 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/17 - Gas loss in Rack 62 channel 17. | ALITOF_Di_DiRack62PCO
ALITOF_Di_62Ch18GLosAl |  | FExx02-06/18 - Rack 62 channel 18 gas loss alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FExx02-06/18 - Gas loss in Rack 62 channel 18. | ALITOF_Di_DiRack62PCO
ALITOF_Di_PT6104_1FT1 |  | PT6104/1 in IO Error or significant deviation between PT6126 and PT6104/1 detected |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | PT6104/1 in IO Error or significant diviation between PT6126 and PT6104/1 detected | ALITOF_Di_DiRack61PCO
ALITOF_Di_PT6204_1FT1 |  | PT6204/1 in IO Error or significant deviation between PT6226 and PT6204/1 detected |  | logic | AL |  |  |  | DigitalAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | PT6204/1 in IO Error or significant diviation between PT6226 and PT6204/1 detected | ALITOF_Di_DiRack62PCO
ALITOF_Xh_AtmPrSensAlDA |  | PT0101 - Atmospheric pressure transmitter alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Xh_AtmPrSensAlDA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | PT0101 - Atmospheric pressure transmitter can not be read. | ALITOF_Xh_XhPCO
ALITOF_Xh_BuPrSensAlDA |  | PT5005 - Buffer pressure sensor alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Xh_BuPrSensAlDA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | PT5005 - Buffer pressure can not be read. | ALITOF_Xh_XhPCO
ALITOF_Xh_DeviceDA |  | Profibus devices alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Xh_DeviceDA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some profibus devices can not be reached. | ALITOF_Xh_XhPCO
ALITOF_Xh_SicWrongRcpDA |  | Inconsistent recipe alarm |  | logic | TS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Xh_SicWrongRcpDA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Inconsistent values in recipes. | ALITOF_Xh_XhPCO
ALITOF_Gs_PCOUnAckAlDA |  | Child to Parent Alarm/interlock UnAcknowledge propagation |  | 0 | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one alarm/interlock of the Parent and Child PCO is not acknowledged | ALITOF_Gs_GsPCO
ALITOF_Gs_AlarmModuleDA |  | Alarms active alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some active alarms. | ALITOF_Gs_GsPCO
ALITOF_Gs_DeviceDA |  | Profibus devices alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some profibus devices can not be reached. | ALITOF_Gs_GsPCO
ALITOF_Gs_DiStopDA |  | Distribution module in Stop alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Distribution module is in Stop. | ALITOF_Gs_GsPCO
ALITOF_Gs_DSSHWIntDA |  | YSL0515 - DSS HW interlock alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | YSL0515 - TOF triggered the DSS HW interlock. | ALITOF_Gs_GsPCO
ALITOF_Gs_PpStopDA |  | Pump module in Stop alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Pump module is in Stop. | ALITOF_Gs_GsPCO
ALITOF_Gs_XhNotInRunDA |  | Exhaust module not in Run alarm |  | logic | FS |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Exhaust module not in Run. | ALITOF_Gs_GsPCO
ALITOF_Gs_MxNotInCompDA |  | Mixer not in compliant state alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Mixer module is not in the required state for a vented system. | ALITOF_Gs_GsPCO
ALITOF_Gs_MxNotInRunDA |  | Mixer not in Run alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Mixer module not in Run. | ALITOF_Gs_GsPCO
ALITOF_Gs_P1NotInNRunDA |  | Purifier module 1 not in Run alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Purifier module 1 not in Nominal Run. | ALITOF_Gs_GsPCO
ALITOF_Gs_ElecStDA |  | Problem detected on Power Supply Rack – check Electrical Status |  | 1 | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Problem detected on Power Supply Rack – check Electrical Status | ALITOF_Gs_GsPCO
ALITOF_Gs_ELMBStDA |  | Problem detected on ELMB Power Supply Rack – check ELMB Status |  | 1 | AL |  |  |  | DigitalAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Problem detected on ELMB Power Supply Rack – check ELMB Status | ALITOF_Gs_GsPCO
ALITOF_Gs_SpareDA1 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA2 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA3 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA4 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA5 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA6 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA7 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA8 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA9 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA10 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA11 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA12 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA13 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA14 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA15 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA16 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA17 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA18 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA19 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Gs_SpareDA20 |  | Spare DA |  | 0 | AL |  |  |  | DigitalAlarm |  |  |  | FALSE | TOF_Details | TOF_Details |  |  | No | [5 empty] | Alarm
ALITOF_Mx_DeviceDA |  | Profibus communication alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Mx_DeviceDA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some profibus devices are no longer accessible. | ALITOF_Mx_MxPCO
ALITOF_Mx_ExtFlamGasDA |  | ZSH9119 - External HW interlock alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Mx_ExtFlamGasDA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | ZSH9119 - External HW interlock triggered. | ALITOF_Mx_MxPCO
ALITOF_Mx_PCOUnAckAlDA |  | Child to Parent Alarm/interlock UnAcknowledge propagation |  | 0 | AL |  | TRUE |  | DigitalAlarm |  | ALITOF/ALITOF_Mx_PCOUnAckAlDA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one alarm/interlock of the Parent and Child PCO is not acknowledged | ALITOF_Mx_MxPCO
ALITOF_Mx_SicFScaleDA |  | Recipe FullScale alarm |  | logic | TS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Mx_SicFScaleDA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some recipe MFC full scale values are null (or negative). | ALITOF_Mx_MxPCO
ALITOF_Pp_DeviceDA |  | Profibus devices alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Pp_DeviceDA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some profibus devices can not be reached. | ALITOF_Pp_PpPCO
ALITOF_Pp_P4101DefDisDA |  | Pump4101 Circuit breaker tripped |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Pp_Pump4101DA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Pump4101 Circuit breaker tripped | ALITOF_Pp_PpPCO
ALITOF_Pp_P4201DefDisDA |  | Pump4201 Circuit breaker tripped |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_Pp_Pump4201DA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison |  |  |  | unProcessAlarm |  | Alarm | Pump4201 Circuit breaker tripped | ALITOF_Pp_PpPCO
ALITOF_P1_AlarmModuleDA |  | Alarms in module alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Module is in alarm. | ALITOF_P1_P1PCO
ALITOF_P1_AllColIntDA |  | Both columns instart interlock alarm |  | logic | SI |  |  |  | DigitalAlarm |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Both columns with start interlock | ALITOF_P1_P1PCO
ALITOF_P1_CAAlarmDA |  | Column A active alarms alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAAlarmDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column A active alarms. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBAlarmDA |  | Column B active alarms alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBAlarmDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column B active alarms. | ALITOF_P1_P1CBPCO
ALITOF_P1_CADisableDA |  | Column A blocked alarms alarm |  | logic | SI |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CADisableDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column A blocked alarms. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBDisableDA |  | Column B blocked alarms alarm |  | logic | SI |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBDisableDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column B blocked alarms. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAHWintlockDA |  | XSSxy01 - Column A HW interlock alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAHWintlockDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | XSSxy01 - Column A HW interlock triggered. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBHWintlockDA |  | XSSxy01 - Column B HW interlock alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBHWintlockDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | XSSxy01 - Column B HW interlock triggered. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAInValvNCDA |  | YVwxt03 - Column A input valve not closed alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAInValvNCDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt03 - Column A input valve could not be closed. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBInValvNCDA |  | YVwxt03 - Column B input valve not closed alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBInValvNCDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt03 - Column B input valve could not be closed. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAInValvNODA |  | YVwxt03 - Column A input valve not open alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAInValvNODA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt03 - Column A input valve could not be open. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBInValvNODA |  | YVwxt03 - Column B input valve not open alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBInValvNODA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt03 - Column B input valve could not be open. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAInValvRDA |  | ZSwxt03 - Column A input valve position read alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAInValvRDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | ZSwxt03 - Column A input valve Open/Close position cannot be read. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBInValvRDA |  | ZSwxt03 - Column B input valve position read alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBInValvRDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | ZSwxt03 - Column B input valve Open/Close position cannot be read. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAnoCDTimerDA |  | TExy01/1-3 - Column A coold down timer alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAnoCDTimerDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | TExy01/1-3 - Column A could not be cooled to its nominal temperature. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBnoCDTimerDA |  | TExy01/1-3 - Column B coold down timer alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBnoCDTimerDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | TExy01/1-3 - Column B could not be cooled to its nominal temperature. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAnoHUPTimeDA |  | TExy01/1-3 - Column A heat up timer alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAnoHUPTimeDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | TExy01/1-3 - Column A could not be heated to its nominal temperature. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBnoHUPTimeDA |  | TExy01/1-3 - Column B heat up timer alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBnoHUPTimeDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | TExy01/1-3 - Column B could not be heated to its nominal temperature. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAnoPurgeDA |  | FISxy12 - Column A no purge gas alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAnoPurgeDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FISxy12 - Column A insufficient purge gas flow. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBnoPurgeDA |  | FISxy12 - Column B no purge gas alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBnoPurgeDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FISxy12 - Column B insufficient purge gas flow. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAnoRegenDA |  | FISxy12 - Column A no regeneration gas alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAnoRegenDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FISxy12 - Column A insufficient regeneration gas flow. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBnoRegenDA |  | FISxy12 - Column B no regeneration gas alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBnoRegenDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | FISxy12 - Column B insufficient regeneration gas flow. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAOutValvNCDA |  | YVwxt07 - Column A output valve not closed alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAOutValvNCDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt07 - Column A output valve could not be closed. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBOutValvNCDA |  | YVwxt07 - Column B output valve not closed alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBOutValvNCDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt07 - Column B output valve could not be closed. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAOutValvNODA |  | YVwxt07 - Column A output valve not open alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAOutValvNODA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt07 - Column A output valve could not be open. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBOutValvNODA |  | YVwxt07 - Column B output valve not open alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBOutValvNODA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | YVwxt07 - Column B output valve could not be open. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAOutValvRDA |  | ZSwxt07 - Column A output valve position read alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAOutValvRDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | ZSwxt07 - Column A output valve Open/Close position cannot be read. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBOutValvRDA |  | ZSwxt07 - Column B output valve position read alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBOutValvRDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | ZSwxt07 - Column B output valve Open/Close position cannot be read. | ALITOF_P1_P1CBPCO
ALITOF_P1_CApSByTimerDA |  | PTxy08 - Column A (PSby)pressure timer alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CApSByTimerDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | PTxy08 - Column A could not be pressurized. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBpSByTimerDA |  | PTxy08 - Column B (PSby)pressure timer alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBpSByTimerDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | PTxy08 - Column B could not be pressurized. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAslowHUpDA |  | TExy01/1-3 - Column A slow heating alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAslowHUpDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | TExy01/1-3 - Column A is not heating fast. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBslowHUpDA |  | TExy01/1-3 - Column B slow heating alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBslowHUpDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | TExy01/1-3 - Column B is not heating fast. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAnotClosedDA |  | Column A output valve open while not in run alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAnotClosedDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column A has its output valve open while not in Run. | ALITOF_P1_P1PCO
ALITOF_P1_CAnotCyclDA |  | Column A is not cycling alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CAnotCyclDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column A is offline. | ALITOF_P1_P1PCO
ALITOF_P1_CBnotClosedDA |  | Column B output valve open while not in run alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBnotClosedDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column B has its output valve open while not in Run. | ALITOF_P1_P1PCO
ALITOF_P1_CBnotCyclDA |  | Column B is not cycling alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CBnotCyclDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Column B is offline. | ALITOF_P1_P1PCO
ALITOF_P1_ColSynchAl |  | Purifier Columns not synchronized alarm |  | logic | AL |  |  |  | DigitalAlarm |  |  | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Purifier Columns not synchronized alarm | ALITOF_P1_P1PCO
ALITOF_P1_CtlnotCyclDA |  | (Single column) Controlled column is not cycling alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_CtlnotCyclDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Controlled column is offline. | ALITOF_P1_P1PCO
ALITOF_P1_DeviceDA |  | Profibus devices alarm |  | logic | FS |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_DeviceDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Some profibus devices can not be reached. | ALITOF_P1_P1PCO
ALITOF_P1_NoColumnRunDA |  | Columns in Stop alarm |  | logic | AL |  |  |  | DigitalAlarm |  | ALITOF/ALITOF_P1_NoColumnRunDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | Both columns are in Stop. | ALITOF_P1_P1PCO
ALITOF_P1_PCOUnAckAlDA |  | Child to Parent Alarm/interlock UnAcknowledge propagation |  | 0 | AL |  | TRUE |  | DigitalAlarm |  | ALITOF/ALITOF_P1_PCOUnAckAlDA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  |  | Old/New Comparison | [5 empty] | Alarm | At least one alarm/interlock of the Parent and Child PCO is not acknowledged | ALITOF_P1_P1PCO

## AnalogAlarm
Name | AnalogAlarm
Package | CPC
Object Type Family | ControlObjectFamily
Description | Analog Alarm Device
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | FEDeviceManualRequests |  |  |  | FEDeviceAlarm |  |  |  | FEDeviceEnvironmentInputs | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  | LogicDeviceDefinitions
[20 empty] | SCADADeviceClassificationTags | [5 empty] | Interlock Archiving | Alarm Config |  |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Remarks | Alarm Delay (s) | HH Alarm | H Warning | L Warning | LL Alarm | Type | Multiple Types | Auto Acknowledge | Enable Condition | Input | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Archive Mode | SMS Category | Masked | Level | Message | Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10
ALITOF_Di_61ChamPRegAA |  | PTxx04 - Rack 61 chamber pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Di_PT6104 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PTxx04 - Rack 61 chamber pressure is out of ranges. | ALITOF_Di_DiRack61PCO
ALITOF_Di_62ChamPRegAA |  | PTxx04 - Rack 62 chamber pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Di_PT6204 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PTxx04 - Rack 62 chamber pressure is out of ranges. | ALITOF_Di_DiRack62PCO
ALITOF_Di_61InPresAl |  | PTxx24 - Rack 61 input pressure alarm |  | logic | 8 | 7 | 1 | 0 | FS |  |  |  | ALITOF_Di_PT6124 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PTxx24 - Rack 61 input pressure is out of ranges. | ALITOF_Di_DiRack61PCO
ALITOF_Di_62InPresAl |  | PTxx24 - Rack 62 input pressure alarm |  | logic | 8 | 7 | 1 | 0 | FS |  |  |  | ALITOF_Di_PT6224 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PTxx24 - Rack 62 input pressure is out of ranges. | ALITOF_Di_DiRack62PCO
ALITOF_Di_61OutPresFAA |  | PTxx26 - Rack 61 far output pressure alarm |  | logic | 3.5 | 3 | 1 | 0 | FS |  |  |  | ALITOF_Di_PT6126 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PTxx26 - Rack 61 far output pressure out of ranges. | ALITOF_Di_DiRack61PCO
ALITOF_Di_62OutPresFAA |  | PTxx26 - Rack 62 far output pressure alarm |  | logic | 2.2 | 1.5 | 1 | 0 | FS |  |  |  | ALITOF_Di_PT6226 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PTxx26 - Rack 62 far output pressure out of ranges. | ALITOF_Di_DiRack62PCO
ALITOF_Di_61PRegAl |  | PCVxx26 - Rack 61 pressure regulation alarm |  | logic | logic | logic | logic | logic | AL |  |  |  |  | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PCVxx26 - Rack 61 pressure regulation is out of ranges. | ALITOF_Di_DiRack61PCO
ALITOF_Di_62PRegAl |  | PCVxx26 - Rack 62 pressure regulation alarm |  | logic | logic | logic | logic | logic | AL |  |  |  |  | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PCVxx26 - Rack 62 pressure regulation is out of ranges. | ALITOF_Di_DiRack62PCO
ALITOF_Di_AtmPressAA |  | PT0201 - Atmospheric pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Gs_PT0201 | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT0201 - Atmospheric pressure out of ranges. | ALITOF_Di_DiPCO
ALITOF_Di_PCV6126RLimAl |  | PCV6126 - Distribution pressure regulation valve limit reached |  | logic | 100.0 |  |  | 0.0 | AL |  |  |  |  | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PCV6126 - Distribution pressure regulation valve limit reached. | ALITOF_Di_DiRack61PCO
ALITOF_Di_PCV6226RLimAl |  | PCV6226 - Distribution pressure regulation valve limit reached |  | logic | 100.0 |  |  | 0.0 | AL |  |  |  |  | AnalogAlarm |  |  | Distribution_FA¦https://edms.cern.ch/file/2000856/1.0/Functional_Analysis_LHC_GCS_Distribution_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PCV6226 - Distribution pressure regulation valve limit reached. | ALITOF_Di_DiRack62PCO
ALITOF_Xh_AtmPressAA |  | PT0101 - Atmospheric pressure alarm |  | logic | logic | logic | logic | logic | AL |  |  |  | ALITOF_Gs_PT0101 | AnalogAlarm |  | ALITOF/ALITOF_Xh_AtmPressAA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details |  | ALITOF_Gs_PT0101 |  |  |  | Old/New Comparison |  |  | Alarm | PT0101 - Atmospheric pressure transmitter out of ranges. | ALITOF_Xh_XhPCO
ALITOF_Xh_BuPrAlAA |  | PT5005 - Buffer pressure alarm |  | logic | logic | logic | logic | logic | AL |  |  |  | ALITOF_Xh_PT5005 | AnalogAlarm |  | ALITOF/ALITOF_Xh_BuPrAlAA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT5005 - Buffer pressure is out of ranges. | ALITOF_Xh_XhPCO
ALITOF_Xh_PDT5030AA |  | PDT5030 - Exhaust filter clogged |  | ALITOF_Xh_PDT5030Dt | 8 | 7 |  |  | AL |  |  | ALITOF_Xh_PDT5030>-10.0 | ALITOF_Xh_PDT5030 | AnalogAlarm |  | ALITOF/ALITOF_Xh_PDT5030AA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT5005 - Buffer pressure is out of ranges. | ALITOF_Xh_XhPCO
ALITOF_Xh_CiPrAlAA |  | PT5011 - Circulation pressure alarm |  | logic | logic | logic | logic | logic | AL |  |  |  | ALITOF_Xh_PT5011 | AnalogAlarm |  | ALITOF/ALITOF_Xh_CiPrAlAA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT5011 - Circulation pressure is out of ranges. | ALITOF_Xh_XhPCO
ALITOF_Xh_PrRegAlAA |  | XMFC5002 - Pressure regulation alarm |  | logic | logic | logic | logic | logic | AL |  |  |  | ALITOF_Xh_PrRDAS | AnalogAlarm |  | ALITOF/ALITOF_Xh_PrRegAlAA_Logic.xml | Exhaust_FA¦https://edms.cern.ch/file/2008217/1.0/Functional_Analysis_LHC_GCS_Exhaust_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC5002 - Buffer pressure regulation is out of ranges. | ALITOF_Xh_XhPCO
ALITOF_Gs_PS24VSurIAA |  | Surface 24VDC power supply module current consumption too high |  | ALITOF_Gs_PSAADt | 25 |  |  |  | AL |  |  |  | ALITOF_Gs_IT24VDCSur | AnalogAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | Surface 24VDC power supply module current consumption too high | ALITOF_Gs_GsPCO
ALITOF_Gs_PS24VCavIAA |  | Cavern 24VDC power supply module current consumption too high |  | ALITOF_Gs_PSAADt | 25 |  |  |  | AL |  |  |  | ALITOF_Gs_IT24VDCCav | AnalogAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | Cavern 24VDC power supply module current consumption too high | ALITOF_Gs_GsPCO
ALITOF_Gs_PS18VCavIAA |  | Cavern 18VDC power supply module current consumption too high |  | ALITOF_Gs_PSAADt | 25 |  |  |  | AL |  |  |  | ALITOF_Gs_IT18VDCCav | AnalogAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | Cavern 18VDC power supply module current consumption too high | ALITOF_Gs_GsPCO
ALITOF_Gs_PS18VCavVAA |  | Cavern 18VDC power supply module voltage level alarm |  | ALITOF_Gs_PSAADt | 21 |  |  | 15 | AL |  |  |  | ALITOF_Gs_18VDCCav | AnalogAlarm |  |  | GasSystem_FA¦https://edms.cern.ch/file/2025447/1.0/Functional_Analysis_LHC_GCS_Gas_System_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | Cavern 18VDC power supply module voltage level alarm | ALITOF_Gs_GsPCO
ALITOF_Gs_SpareAA1 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA2 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA3 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA4 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA5 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA6 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA7 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA8 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA9 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Gs_SpareAA10 |  | Spare |  | 0 |  |  |  |  | AL |  |  |  |  | AnalogAlarm |  |  |  | FALSE | TOF_Details | TOF_Details | [5 empty] | No |  |  | Alarm
ALITOF_Mx_L1PressAA |  | PT1103 - Low pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Mx_PT1103 | AnalogAlarm |  | ALITOF/ALITOF_Mx_L1PressAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT1103 - Gas 1 pressure too low. | ALITOF_Mx_MxPCO
ALITOF_Mx_L2PressAA |  | PT1203 - Low pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Mx_PT1203 | AnalogAlarm |  | ALITOF/ALITOF_Mx_L2PressAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT1203 - Gas 2 pressure too low. | ALITOF_Mx_MxPCO
ALITOF_Mx_L3PressAA |  | PT1303 - Low pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Mx_PT1303 | AnalogAlarm |  | ALITOF/ALITOF_Mx_L3PressAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT1303 - Gas 3 pressure too low. | ALITOF_Mx_MxPCO
ALITOF_Mx_L1NotRelAA |  | XMFC110x - (Fill/Run) Master gas flow alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L1NotRelAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC110x - Flow 1 out of reliable measurement limits. | ALITOF_Mx_MxPCO
ALITOF_Mx_L2NotRelAA |  | XMFC120x - (Fill/Run) Master gas flow alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L2NotRelAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC120x - Flow 2 out of reliable measurement limits. | ALITOF_Mx_MxPCO
ALITOF_Mx_L3NotRelAA |  | XMFC130x - (Fill/Run) Master gas flow alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L3NotRelAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC130x - Flow 3 out of reliable measurement limits. | ALITOF_Mx_MxPCO
ALITOF_Mx_L1CompRatioAA |  | XMFC110x - (Fill/Run) Computed ratio deviation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L1CompRatioAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC110x - Gas 1 computed ratio regulation out of ranges. | ALITOF_Mx_MxPCO
ALITOF_Mx_L2CompRatioAA |  | XMFC120x - (Fill/Run) Computed ratio deviation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L2CompRatioAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC120x - Gas 2 computed ratio regulation out of ranges. | ALITOF_Mx_MxPCO
ALITOF_Mx_L3CompRatioAA |  | XMFC130x - (Fill/Run) Computed ratio deviation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L3CompRatioAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC130x - Gas 3 computed ratio regulation out of ranges. | ALITOF_Mx_MxPCO
ALITOF_Mx_L1WrongFlowAA |  | Flow detected on non-selected Mixer line XMFC110x |  | logic | logic | logic | logic | logic | AL |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L1WrongFlowAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | Flow detected on non-selected Mixer line XMFC110x | ALITOF_Mx_MxL1PCO
ALITOF_Mx_L2WrongFlowAA |  | Flow detected on non-selected Mixer line XMFC120x |  | logic | logic | logic | logic | logic | AL |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L2WrongFlowAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | Flow detected on non-selected Mixer line XMFC120x | ALITOF_Mx_MxL2PCO
ALITOF_Mx_L3WrongFlowAA |  | Flow detected on non-selected Mixer line XMFC130x |  | logic | logic | logic | logic | logic | AL |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L3WrongFlowAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | Flow detected on non-selected Mixer line XMFC130x | ALITOF_Mx_MxL3PCO
ALITOF_Mx_L1FlowRegAA |  | XMFC110x - (Direct/Purge) Flow regulation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L1FlowRegAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC110x - Gas 1 flow regulation is out of ranges. | ALITOF_Mx_MxPCO
ALITOF_Mx_L2FlowRegAA |  | XMFC120x - (Direct/Purge) Flow regulation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L2FlowRegAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC120x - Gas 2 flow regulation is out of ranges. | ALITOF_Mx_MxPCO
ALITOF_Mx_L3FlowRegAA |  | XMFC130x - (Direct/Purge) Flow regulation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L3FlowRegAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC130x - Gas 3 flow regulation is out of ranges. | ALITOF_Mx_MxPCO
ALITOF_Mx_L1FlowAA |  | XMFC110x - (Fill/Run) Master gas flow alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Mx_L1FlowAA_Logic.xml | Mixer_FA¦https://edms.cern.ch/file/1995143/1.0/Functional_Analysis_LHC_GCS_Mixer_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | XMFC110x - Master component gas flow is not high enough. | ALITOF_Mx_MxPCO
ALITOF_Pp_PmP1TH1AA |  | TE4101/1 - Pump too hot alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Pp_TE4101_1 | AnalogAlarm |  | ALITOF/ALITOF_Pp_PmP1TH1AA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TE4101/1 - Temperature of circulation pump 1 engine is too high. | ALITOF_Pp_PpPCO
ALITOF_Pp_PmP2TH1AA |  | TE4201/1 - Pump too hot alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Pp_TE4201_1 | AnalogAlarm |  | ALITOF/ALITOF_Pp_PmP2TH1AA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TE4201/1 - Temperature of circulation pump 2 engine is too high. | ALITOF_Pp_PpPCO
ALITOF_Pp_PressRegAA |  | PV4003 - Pressure regulation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Pp_PressRegAA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PV4003 - Pressure regulation out of ranges. | ALITOF_Pp_PpPCO
ALITOF_Pp_SWPressAA |  | PT4004 - Soft. pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Pp_PT4004 | AnalogAlarm |  | ALITOF/ALITOF_Pp_SWPressAA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PT4004 - Input pressure out of ranges. | ALITOF_Pp_PpPCO
ALITOF_Pp_PV4003RLimAl |  | PV4003 Pump pressure regulation valve limit reached |  | logic | 90 |  |  | 10 | AL |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_Pp_PressRegAA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | PV4003 Pump pressure regulation valve limit reached | ALITOF_Pp_PpPCO
ALITOF_Pp_PmP1Press1AA |  | PT4101/1 - Membrane head first pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Pp_PT4101_1 | AnalogAlarm |  | ALITOF/ALITOF_Pp_PmP1Press1AA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | PT4101/1 - The first head membrane pressure of pump1 is out of ranges. | ALITOF_Pp_PpPCO
ALITOF_Pp_PmP2Press1AA |  | PT4201/1 - Membrane head first pressure alarm |  | logic | logic | logic | logic | logic | FS |  |  |  | ALITOF_Pp_PT4201_1 | AnalogAlarm |  | ALITOF/ALITOF_Pp_PmP2Press1AA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | PT4201/1 - The first head membrane pressure of pump2 is out of ranges. | ALITOF_Pp_PpPCO
ALITOF_Pp_PDT4020AA |  | Pump module outlet filter clogged |  | logic | 20 | 15 |  |  | AL |  |  |  | ALITOF_Pp_PDT4020 | AnalogAlarm |  | ALITOF/ALITOF_Pp_PressRegAA_Logic.xml | https://edms.cern.ch/ui/file/2005604/1.0/Functional_Analysis_LHC_GCS_Pump_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison | unProcessAlarm:NO_SMS_ON_WARNING,unProcessWarning:NO_SMS_ON_ALERT |  | Alarm | Pump module outlet filter clogged | ALITOF_Pp_PpPCO
ALITOF_P1_CARunHotAA |  | TExy01/1-3 - Column A internal temperature alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_P1_CARunHotAA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TExy01/1-3 - Column A internal temperature is too high. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBRunHotAA |  | TExy01/1-3 - Column B internal temperature alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_P1_CBRunHotAA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TExy01/1-3 - Column B internal temperature is too high. | ALITOF_P1_P1CBPCO
ALITOF_P1_CAExtTHotAA |  | TExy01/2 - Column A external temperature alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_P1_CAExtTHotAA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TExy01/2 - Column A external temperature is too high. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBExtTHotAA |  | TExy01/2 - Column B external temperature alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_P1_CBExtTHotAA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TExy01/2 - Column B external temperature is too high. | ALITOF_P1_P1CBPCO
ALITOF_P1_CABadTRegulAA |  | TZxy01 - Column A temperature regulation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_P1_CABadTRegulAA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TZxy01 - Column A temperature regulation out of ranges. | ALITOF_P1_P1CAPCO
ALITOF_P1_CBBadTRegulAA |  | TZxy01 - Column B temperature regulation alarm |  | logic | logic | logic | logic | logic | FS |  |  |  |  | AnalogAlarm |  | ALITOF/ALITOF_P1_CBBadTRegulAA_Logic.xml | Purifier_FA¦https://edms.cern.ch/file/1967437/0/Functional_Analysis_LHC_GCS_Purifier_docx_cpdf.pdf | FALSE | TOF_Details | TOF_Details | [5 empty] | Old/New Comparison |  |  | Alarm | TZxy01 - Column B temperature regulation out of ranges. | ALITOF_P1_P1CBPCO