## Summary
|  | FEType | Global definition
0 | No address
1 | direct access to periphery
100-199 | internal access (memory ioscanning DB, etc ..)
200-299 | Fieldbus Profibus
300-399 | Fieldbus CanOpen
400-499 | Fieldbus Ethernet-IP/ProfibusGateway-M580
Details
Step7: Siemens |  | Unity: Schneider |  | CoDeSys
FEType |  | FEType |  | FEType
0 | No address | 0 | No address | 0 | No address
1 | direct access to periphery | 1 | direct access to periphery | 1 | direct access to periphery
|  | 2 | direct access to periphery without IOSimu
…
|  | 10 | M580 Drop Quantum
100 | internal memory access | 100 | internal memory access | 100 | internal memory access
101 | Read/write: DB without IO Error | 101 | Ioscanning
102 | Read/write: DB with IO Error | 102 | Ioscanning1
103 | Read/write: DB with inverted IO Error | 103 | GlobalData
|  | 104 | GlobalData1
200 |  | 200 | Read/Write Profibus, use 401 for M580 + PRM
201 | Read/Write PA valve in Profibus DP with 10 bytes consistency check | 201 | Read/Write Profibus Byte Array, use 401 for M580 + PRM
202 | Reading from Profibus PA sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | 202 | Read/Write Profibus word Array, use 401 for M580 + PRM
203 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | 203 | Read/write Profibus Wago
204 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation) | 204 | Read/write Profibus Siemens (specific), use 401 for M580 + PRM
205 | Read/Write Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | 205 | Read/write Profibus Bronkhorst
|  | 2xx | Read/write Profibus xx
|  | 225 | Read/write via IO objects : Bronkhorst
|  | 300 | CanOpen Interface
|  | 301 | Read/write CanOpenCPP_ELMB
|  | 400 | Read/Write Ethernet IP | 400 | Read/Write EtherCat /Ethernet IP
|  | 401 | Read/Write Profibus M580 and PRM
Where XXX being a specifity of this product

## Schneider
Schneider FE Device IO Configuration
| FE_TYPE | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10
Analog Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel %IW\2.20\0.0.0.1 %IW\2.1\0.2.7 | Module Type - AMI0800 |  |  |  | Node Status %I\2.20\0.0.0.ERR - |  | Other error My_IOError - | RawError in % 2 | Extra Type symbols | Periphery Syntax 1 Periphery Syntax 2 (M580 with Non-Topological addressing, automatically convert topological addresses to symbolic addresses generated by Unity Pro) ONLY WORKS with UNITY Pro V13 minimum
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax %IW0.9.0; Schneider FE Device IO Configuration Param6: Node Status %IW0.9.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError; Schneider FE Device IO Configuration Param9: RawError in % 2 | Periphery Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: Address %I120; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | Periphery for QUANTUM Ioerror
| 2 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel %IW\2.20\0.0.0.1; Schneider FE Device IO Configuration Param6: Node Status %I\2.20\0.0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError; Schneider FE Device IO Configuration Param9: RawError in % 2 | Periphery without IOSimu
| 10 | Schneider FE Device IO Configuration Param1: Address %I120; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | M580 with Quantum DROPS with IOE
| 20 | Schneider FE Device IO Configuration Param1: Address or Symbol %MW1000 MYWORD; Schneider FE Device IO Configuration Param8: Other error %M2.9 SYMBOLIOERROR; Schneider FE Device IO Configuration Param9: IOSimu %M2.3 SYMBOLIOSIMU | Internal (%MW) Syntax 1 : %MWxxxx Syntax 2: Any WORD/INT (MYWORD) variable or complex WORD formula: %IW2.1.0.1 + 10.0)/7.0
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal old syntax Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 101 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for IOScanning Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 103 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for Global Data Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 200 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 203 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - - | First address - 0 100 Card Name 2nd Part | Offset - 0 10 4 | Index - 1 5 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError | if M580 with ETH-IP - - - BMEP58 | IOType pby472 pby472 dtm Card Name 1st Part | Profibus PBY or Any DTM with Wago, card type: pby472 = 0-20mA pby474 = 4-20mA pby452 = 0-20mA pby454 = 4-20mA pby455 = 4-20mA pby468 = 0-10V pby485 = 4-20mA pby460 = 4CH PT100 pby461 = 2CH PT100 pby469 = 2 TC type K pby482/484 = 4-20mA pby472s/474s/461s = 24bits format dtm: %MW115 BMEP58(M580+ETH-IP symbols): MOD_ANA_"Param10"_"Param2".ANA_CH_IN[" Param3"].ANA.VALUE
| 204 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - 1.7.0 | First address - 0 100 0 | Offset - 0 10 0 | Index - 1 5 1 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of VFD - - - %IW1.7.0.150.8 | Other error My_IOError |  | IOType pby pby dtm pbymm420 | Same as 200 type but with one more specific case for Siemens VFD in Profibus (pbymm420)
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3]
| 402 | Symbol Name in Eth-IP DTM WAGO.Inputs.free0 | First Byte/Word Array Offset 3 |  |  |  | ETH IP device number (for IOError) 518 | Array Type (Byte or Word or Int) Byte | IoError based on RawRange (%) 5 -4,7 | if M580 with ETH-IP, has to be name of ETH port name in DTM BMEP58_ECPU_EXT | IOType 455 | Ethernet-IP with M580 and DTM symbols (DIO) Ex: WAGO.Inputs.free0[3] For details regarding Param6, see picture on the right Regarding Param10, if module is Wago, input the module model number, If module is generic input nothing Param7 only used if not Wago or Festo, Param8 is the tolerance value to trigger IOError, can be a negative value to trigger within the range or/and declare 2 different tolerance for min and max
Analog Input Real | 0 | [10 empty] | No address
| 20 | Schneider FE Device IO Configuration Param1: Address or Symbol %MW1000 MYREAL; Schneider FE Device IO Configuration Param8: Other error %M2.9 SYMBOLIOERROR; Schneider FE Device IO Configuration Param9: IOSimu %M2.3 SYMBOLIOSIMU | Internal (%MW) Syntax 1 : %MWxxxx Syntax 2: Any REAL (MYREAL) variable or complex REAL formula: DINT_TO_REAL(%ID2.1.0.1 + 10.0)/7.0)
| 100 | Rack.Slot. Channel or Header - %MF115 %MW115 | First address 100 - - | Offset 10 - - | Index 5 - |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal (%MF) Write in memory (%MF works only with PREMIUM anq QUANTUM PLCs, can't be used with M340 and M580) Syntax 1 : %MF115 (100+10+5) Syntax2 :HFPos ->%MF115 Syntax3 (M340/M580) : HFPos ->%MW115
| 101 | Rack.Slot. Channel or Header - 115 100 %MW115 | First address 100 - 15 - | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  | If M580 m580 m580 - | Same as 100 but for IoScanning, with M580: declare a Symbolic real with the address set in spec (%MW115) and add "m580" in param10 Or assign address to HFPos Syntax3 (M340/M580): HFPos ->%MW115
| 103 | Rack.Slot. Channel or Header - %MF115 %MW115 | First address 100 - - | Offset 10 - - | Index 5 - - |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Same as 100 but for GlobalData (%MF) Write in memory (%MF works only with PREMIUM anq QUANTUM PLCs, can't be used with M340 and M580) Syntax 1 : %MF115 (100+10+5) Syntax2 :HFPos ->%MF115 Syntax3 (M340/M580) : HFPos ->%MW115
| 110 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error |  |  | Internal M580 Quantum (%MF)
| 200 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby - dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 204 | Rack.Slot. Channel or Header or Sipart 1st Word %IW1.7.0.1 1.7.0 - %IW1.8.0.0 1.8.0 %MW10 10 | First address or Sipart 2nd Word - 0 100 %IW1.8.0.1 0 %MW11 0 | Offset - 0 10 - 0 - 0 | Index - 1 5 - 0 - 0 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of Module %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y - | Other error My_IOError |  | IOType pby pby dtm pbysipart pbysipart dtmsipart dtmsipart | Same as 200 type but with endian management and Siemens SIPART valve in Profibus (use conversion "CONV_Siemens") PBY Syntax 1 (%IW) PBY Syntax 2 (%IW) DTM Syntax (%MW) PBY Sipart Syntax 1 PBY Sipart Syntax 2 DTM Sipart Syntax 1 DTM Sipart Syntax 2
| 205 | Rack.Slot. Channel or Header or Bronkhorst 1st Word %IW1.7.0.1 1.7.0 - - - | First address or Sipart 2nd Word - 0 100 100 100 | Offset - 0 10 15 15 | Index - 1 5 - - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  |  |  | IOType pby pby dtm pbyfm dtmfm | Same as 200 type but with endian management and Bronkhorst Flowmeter in Profibus (use conversion "CONV_Siemens") PBY Syntax 1 (%IW) PBY Syntax 2 (%IW) DTM Syntax (%MW) PBY Bronk FM Syntax DTM Bronk FM Syntax
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4; Schneider FE Device IO Configuration Param7: Little Endian/Big Endian (Words) normal or inverted | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3]
| 402 | Schneider FE Device IO Configuration Param1: Symbol Name in Eth-IP DTM MyDevice.Inputs.free0; Schneider FE Device IO Configuration Param2: First Byte/Word/Real Array Offset 3; Schneider FE Device IO Configuration Param6: ETH IP device number (for IOError) 518; Schneider FE Device IO Configuration Param7: Array Type (Byte or Word or Real) Byte; Schneider FE Device IO Configuration Param9: if M580 with ETH-IP, has to be name of ETH port name in DTM BMEP58_ECPU_EXT | Ethernet-IP with M580 and DTM symbols (DIO) Ex: MyDevice.Inputs.free0[3] For details regarding Param6, see picture on the right Regarding Param10, if module is Wago, input the module model number, If module is generic input nothing Param7 only used if not Wago or Festo,
Analog Output | 0 | [10 empty] | No address
| 1 | Rack.Slot. Channel 1.7.0 1.7 %QW\2.1\0.2.3 | First address - - AMO0410 | Offset - - | Index - 0 |  | Node Status %I1.7.0.ERR %I1.7.0.ERR - |  | Other error My_IOError - |  | Extra Type symbols | Periphery Syntax 1 Syntax 2 Syntax 3 (M580 with Non-Topological addressing, automatically convert topological addresses to symbolic addresses generated by Unity Pro) ONLY WORKS with UNITY Pro V13 minimum
| 1 | Old Syntax %QW1.7.0 | First address - | Offset - | Index - |  | Node Status %I1.7.0.ERR |  | Other error My_IOError |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: Address %MW30010; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | Periphery for QUANTUM Ioerror
| 10 | Schneider FE Device IO Configuration Param1: Address %MW30010; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | M580 with Quantum DROPS with IOE
| 20 | Schneider FE Device IO Configuration Param1: Address or Symbol %MW1000 MYWORD; Schneider FE Device IO Configuration Param8: Other error %M2.9 SYMBOLIOERROR; Schneider FE Device IO Configuration Param9: IOSimu %M2.3 SYMBOLIOSIMU | Internal (%MW) Syntax 1 : %MWxxxx Syntax 2: Any WORD/INT (MYWORD) variable
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal old syntax Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 101 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for IOScanning Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 103 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for Global Data Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 200 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 203 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError | if M580 with ETH-IP - - - | IOType pby553 pby553 dtm | Profibus PBY or Any DTM with Wago, card type: pby553 pby555 dtm: %MW115
| 204 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - 1.7.0 | First address - 0 100 0 | Offset - 0 10 0 | Index - 1 5 1 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of VFD - - - %IW1.7.0.150.8 | Other error My_IOError |  | IOType pby pby dtm pbymm420 | Same as 200 type but with one more specific case for Siemens VFD in Profibus (pbymm420)
| 400 | Schneider FE Device IO Configuration Param1: Symbol of Card name in DTM MycardName -; Schneider FE Device IO Configuration Param2: First byte array address 0 Card Name 2nd Part; Schneider FE Device IO Configuration Param3: Offset - 0; Schneider FE Device IO Configuration Param9: EndSwitch ETC101 BMEP580301; Schneider FE Device IO Configuration Param10: IOType 553 Card Name 1st Part | Ethernet-IP with M580 + Wago I/O modules if Param9=ETC101 -> NodeSt build from Param2,Param6 and Param9, see template for more details, MOD_ANA_"Param10"_"Param2".ANA_CH_OUT[" Param3"].ANA.VALUE
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Outputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Outputs.xxxx[3]
| 402 | Symbol Name in ETH-IP DTM WAGO.Outputs.free1 | First Byte/Word Array Offset 3 |  |  | Little Endian/Big Endian (Bytes) normal or inverted | ETH IP device number (for IOError) 518 | Array Type (Byte or Word or Int) Byte |  | if M580 with ETH-IP, has to be name of ETH port name in DTM BMEP58_ECPU_EXT | IOType 555 | Ethernet-IP with M580 and DTM symbols (DIO) Ex: WAGO.Outputs.free1[3] For details regarding Param6, see picture on the right close to Analog Input lines Regarding Param10, if module is Wago, input the module model number, If module is generic input nothing
Analog Output Real | 0 | [10 empty] | No address
| 20 | Schneider FE Device IO Configuration Param1: Address or Symbol %MW1000 MYSYMBOL; Schneider FE Device IO Configuration Param8: Other error %M2.9 SYMBOLIOERROR; Schneider FE Device IO Configuration Param9: IOSimu %M2.3 SYMBOLIOSIMU | Internal (%MW) Syntax 1 : %MWxxxx Syntax 2: Symbolic address
| 100 | Rack.Slot. Channel or Header - %MF115 %MW115 | First address 100 - - | Offset 10 - - | Index 5 - - |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal (%MF) Write in memory (%MF works only with PREMIUM anq QUANTUM PLCs, can't be used with M340 and M580) Syntax 1 : %MF115 (100+10+5) Syntax2 :OutOv ->%MF115 Syntax3 (M340/M580) : OutOv ->%MW115
| 101 | Rack.Slot. Channel or Header - 115 %MW115 | First address 100 - - | Offset 10 - - | Index 5 - - |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  | If M580 m580 - | Same as 100 but for IoScanning, with M580: declare a Symbolic real with the address set in spec (%MW115) and add "m580" in param10 Or assign address to OutOv Syntax3 (M340/M580): OutOv ->%MW115
| 103 | Rack.Slot. Channel or Header - %MF115 %MW115 | First address 100 - - | Offset 10 - - | Index 5 - - |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Same as 100 but for GlobalData (%MF) Write in memory (%MF works only with PREMIUM anq QUANTUM PLCs, can't be used with M340 and M580) Syntax 1 : %MF115 (100+10+5) Syntax2 :OutOv ->%MF115 Syntax3 (M340/M580) : OutOv ->%MW115
| 110 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error |  |  | Internal Quantum (%MF) or M580
| 200 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby - dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 204 | Rack.Slot. Channel or Header or Sipart 1st Word %QW1.7.0.1 1.7.0 - %QW1.8.0.0 1.8.0 %MW10 10 | First address or Sipart 2nd Word - 0 100 %QW1.8.0.1 0 %MW11 0 | Offset - 0 10 - 0 - 0 | Index - 1 5 - 0 - 0 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of Module %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y - | Other error My_IOError |  | IOType pby pby dtm pbysipart pbysipart dtmsipart dtmsipart | Same as 200 type but with endian management and Siemens SIPART valve in Profibus (use conversion "CONV_Siemens") PBY Syntax 1 (%IW) PBY Syntax 2 (%IW) DTM Syntax (%MW) PBY Sipart Syntax 1 PBY Sipart Syntax 2 DTM Sipart Syntax 1 DTM Sipart Syntax 2
| 401 | Symbol Name in Profibus DTM DP_PA_Link_IM157.Outputs.xxxx DP_PA_Link_IM157.Outputs.READBACK_POS_D_CHECKBACK_SP_OUT_1 | First Byte Array Offset 3 0 |  |  | Little Endian/Big Endian (Words) normal or inverted | Profibus Node address (for IOError) 6 | Little Endian/Big Endian (Words) normal or inverted |  |  | IOType if Sipart valve command : - sipart | Profibus Remote Module with M580 and DTM symbols Example generic: DP_PA_Link_IM157.Outputs.xxxx[3] Example with sipart Valve: DP_PA_Link_IM157.Outputs.READBACK_POS_D_CHECKBACK_SP_OUT_1[0]
| 402 | Symbol Name in ETH-IP DTM MyDevice.Outputs.free1 | First Byte/Real Array Offset 3 |  |  | Little Endian/Big Endian (Bytes) normal or inverted | ETH IP device number (for IOError) 518 | Array Type (Byte or Real) Byte |  | if M580 with ETH-IP, has to be name of ETH port name in DTM BMEP58_ECPU_EXT |  | Ethernet-IP with M580 and DTM symbols (DIO) Ex: MyDevice.Outputs.free1[3] For details regarding Param6, see picture on the right close to Analog Input lines Regarding Param10, if module is Wago, input the module model number, If module is generic input nothing
Digital Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel %I0.4.0 %I\2.1\0.4.0 | First address DDI1604 | Offset | Index | Invert | Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR - |  | Other error My_IOError |  | Extra Type symbols | Periphery Syntax 1 Syntax 2 Syntax 3 (M580 with Non-Topological addressing, automatically convert topological addresses to symbolic addresses generated by Unity Pro) ONLY WORKS with UNITY Pro V13 minimum
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax 0.4 \1.2.1\0; Schneider FE Device IO Configuration Param4: Index 0 0; Schneider FE Device IO Configuration Param5: Invert; Schneider FE Device IO Configuration Param6: Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError | Periphery with old syntax Syntax 1 Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel 0.2.0 5.4.0; Schneider FE Device IO Configuration Param4: Profibus/Eth-IP Node 5 -; Schneider FE Device IO Configuration Param10: IOType pby dtm or etc | Periphery with Profibus/ETH-IP and PREMIUM to detect node error on Profibus DP, dtm/etc version use CONV_FieldbusDTM pby syntax dtm syntax
| 1 | Schneider FE Device IO Configuration Param1: PRM Structure name "_PRM_Status" or -; Schneider FE Device IO Configuration Param4: Profibus Node 5; Schneider FE Device IO Configuration Param10: IOType prm ptq | Periphery with PRM and PREMIUM to detect node error on Profibus DP, use FB CONV_FieldbusDTM
| 1 | Schneider FE Device IO Configuration Param1: PRM Structure name "PRM_Gateway.Inputs" or -; Schneider FE Device IO Configuration Param4: Profibus Node 5; Schneider FE Device IO Configuration Param10: IOType prmm580 | Periphery with PRM and M580 to detect node error on Profibus DP, use CONV_FieldbusDTM
| 1 | Schneider FE Device IO Configuration Param1: Address %IW40; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | Periphery for QUANTUM Ioerror
| 10 | Schneider FE Device IO Configuration Param1: Address %IW40; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | M580 with Quantum DROPS with IOE
| 20 | Schneider FE Device IO Configuration Param1: Address %MW100.0 or %M10 SYMBOL; Schneider FE Device IO Configuration Param8: Other error %MW100.0 OR %M5 SYMBOL; Schneider FE Device IO Configuration Param9: IOSimu %M2.3 SYMBOLIOSIMU | Internal (%MW) Syntax 1 : %MWxxxx.y OR %Mx Syntax 2: Symbolic address
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError | IOSimu %M2.3 SYMBOLIOSIMU |  | Internal (%MW) Syntax 1 Syntax 2
| 200 | Rack.Slot. Channel or Header %IW1.7.0 1.7.0 - %MW115.0 | First address - 0 100 - | Offset - 0 15 - | Index - 1 0 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 201 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 203 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 400 | Symbol of Card name in DTM MycardName | First byte array address 0 | Index of bit in byte 3 |  |  | Ioerror 2 |  |  | EndSwitch ETC101 | IOType 402/430 | Ethernet IP bit stored in word array Syntax 1 Param1 + ".free0[" + Param2 + "]." + Param3
| 400 | Schneider FE Device IO Configuration Param2: Symbol of Card name in DTM Card Name 2nd Part; Schneider FE Device IO Configuration Param3: First byte array address 3; Schneider FE Device IO Configuration Param6: Ioerror 2; Schneider FE Device IO Configuration Param9: EndSwitch BMEP580301; Schneider FE Device IO Configuration Param10: IOType Card Name 1st Part | Ethernet IP bit stored in word array Syntax2 " MOD_DIS_" + Param10 + "_" + Param2 + ".DIS_CH_IN[" + Param3 + "].VALUE"
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 1; Schneider FE Device IO Configuration Param4: Index of bit in byte 4; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 5 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[1].4
| 402 | Schneider FE Device IO Configuration Param1: Symbol Name in ETH-IP DTM WAGO.Inputs.free0; Schneider FE Device IO Configuration Param2: First Byte Array Offset 1; Schneider FE Device IO Configuration Param3: Index of bit in byte 4; Schneider FE Device IO Configuration Param6: ETH IP device number (for IOError) 518; Schneider FE Device IO Configuration Param9: if M580 with ETH-IP, has to be name of ETH port name in DTM BMEP58_ECPU_EXT | Ethernet-IP with M580 and DTM symbols (DIO) Ex: WAGO.Inputs.free0[1].4 For details regarding Param6, see picture on the right close to Analog Input lines
Digital Output | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel %Q0.4.0 %Q1.2.1\0.0 %Q\2.1\0.1.0 | First address (Short Name of the I/O Module) DDO3202K | Offset | Index | Invert | Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR - |  | Other error My_IOError |  | Extra Type symbols | Periphery Syntax 1 Syntax 2 Syntax 3 (M580 with Non-Topological addressing, automatically convert topological addresses to symbolic addresses generated by Unity Pro) ONLY WORKS with UNITY Pro V13 minimum
|  | Schneider FE Device IO Configuration Param1: OldSyntax 0.4 \1.2.1\0; Schneider FE Device IO Configuration Param4: Index 0 0; Schneider FE Device IO Configuration Param5: Invert; Schneider FE Device IO Configuration Param6: Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError | Periphery with old syntax Syntax 1 Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: Address %M23; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | Periphery for QUANTUM Ioerror
| 10 | Schneider FE Device IO Configuration Param1: Address %M23; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | M580 with Quantum DROPS with IOE
| 20 | Schneider FE Device IO Configuration Param1: Address %MW100.0 or %M10 SYMBOL; Schneider FE Device IO Configuration Param8: Other error %MW100.0 OR %M5 SYMBOL; Schneider FE Device IO Configuration Param9: IOSimu %M2.3 SYMBOLIOSIMU | Internal (%MW) Syntax 1 : %MWxxxx.y OR %Mx Syntax 2: Symbolic address
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError | IOSimu %M2.3 SYMBOLIOSIMU |  | Internal (%MW) Syntax 1 Syntax 2
| 200 | Rack.Slot. Channel or Header %QW1.7.0 1.7.0 - %MW115.0 | First address - 0 100 - | Offset - 0 15 - | Index - 1 0 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 201 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 202/203 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 204 | Rack.Slot. Channel or Header %QW1.7.0 1.7.0 - %MW115.0 | First address - 0 100 - | Offset - 0 15 - | Index - 1 0 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of VFD %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxx.YY %MWxxx.YY | Other error My_IOError |  | IOType pbymm420 pbymm420 dtmmm420 dtmmm420 | Profibus PBY or Any DTM with Premium + Siemens VFD management, use FB CONV_Siemens PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 400 | Symbol of Card name in DTM MycardName | First byte array address 0 | Index of bit in byte 3 |  |  | Ioerror 2 |  |  | EndSwitch ETC101 | IOType 504/514 /556838 | Premium Ethernet IP bit stored in word array Syntax 1 Param1 + ".free0[" + Param2 + "]." + Param3
| 400 | Schneider FE Device IO Configuration Param2: Symbol of Card name in DTM Card Name 2nd Part; Schneider FE Device IO Configuration Param3: First byte array address 3; Schneider FE Device IO Configuration Param6: Ioerror 2; Schneider FE Device IO Configuration Param9: EndSwitch BMEP580301; Schneider FE Device IO Configuration Param10: IOType Card Name 1st Part | M580 s40 Ethernet IP bit stored in word array Syntax2 " MOD_DIS_" + Param10 + "_" + Param2 + ".DIS_CH_OUT[" + Param3 + "].VALUE"
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Outputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 1; Schneider FE Device IO Configuration Param4: Index of bit in byte 2; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 7 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Outputs.xxxx[1].2
| 402 | Schneider FE Device IO Configuration Param1: Symbol Name in Eth-IP DTM MyDevice.Outputs; Schneider FE Device IO Configuration Param2: First Byte Array Offset 1; Schneider FE Device IO Configuration Param3: Index of bit in byte 2; Schneider FE Device IO Configuration Param6: ETH IP device number (for IOError) 518; Schneider FE Device IO Configuration Param9: if M580 with ETH-IP, has to be name of ETH port name in DTM BMEP58_ECPU_EXT | Ethernet-IP with M580 and DTM symbols (DIO) Ex: MyDevice.Outputs[1].4 For details regarding Param6, see picture on the right close to Analog Input lines
Analog Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address 200; Schneider FE Device IO Configuration Param3: Offset 10; Schneider FE Device IO Configuration Param8: If memory read -; Schneider FE Device IO Configuration Param9: If endian inversion/Normal endian/- | Internal Read memory %MF210
| 100 | Schneider FE Device IO Configuration Param1: Address - %MF230 %MW230; Schneider FE Device IO Configuration Param2: First address 200 - -; Schneider FE Device IO Configuration Param3: Offset 30 - -; Schneider FE Device IO Configuration Param8: If memory write out out out; Schneider FE Device IO Configuration Param9: If endian inversion/Normal endian/- endian/- endian/- | Internal Write in memory (%MF works only with PREMIUM anq QUANTUM PLCs, can't be used with M340 and M580) Syntax 1 : %MF230 Syntax2 :AuPosR ->%MF230 Syntax3 (M340/M580) : AuPosR ->%MW230
| 110 | Schneider FE Device IO Configuration Param1: Symbol Name MySymbol | Specific Symbol Name The _AuPosR is replaced by a specific variable at the input of the AS DFB MySymbol
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Words) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4; Schneider FE Device IO Configuration Param7: Little Endian/Big Endian (Words) normal or inverted | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3]
Word Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address 200 %MW210; Schneider FE Device IO Configuration Param3: Offset 10; Schneider FE Device IO Configuration Param8: If memory read - - | Internal Read memory %MW210
| 100 | Schneider FE Device IO Configuration Param2: First address 200 %MW230; Schneider FE Device IO Configuration Param3: Offset 30; Schneider FE Device IO Configuration Param8: If memory write out out | Internal Write in memory %MW230
| 101 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (IOScanning PREMIUM) Channel 1-16 INT_TO_WORD(%IW" + Param1 + ".3.1)
| 102 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (IOScanning PREMIUM) Channel 16-32 INT_TO_WORD(%IW" + Param1 + ".3.2)
| 103 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (Global Data PREMIUM) Channel 1-16 INT_TO_WORD(%IW" + Param1 + ".3.9)
| 104 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (Global Data PREMIUM) Channel 16-32 INT_TO_WORD(%IW" + Param1 + ".3.10)
| 105 | Schneider FE Device IO Configuration Param2: single bits separated by ",". Put more "," for positioning VAR1,VAR2,0,VAR3 | Internal Single bit management on each Word Bit
| 110 | Schneider FE Device IO Configuration Param1: Symbol Name MySymbol | Specific Symbol Name The _AuPosR is replaced by a specific variable at the input of the WS DFB MySymbol
| 200 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pby pby dtm dtm | Profibus access PBY/DTM PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 204 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pby pby dtm dtm | Profibus access PBY/DTM with lower/upper byte (endian) rotation - use for CPC5 type 10 Sipart valve checkback PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 204 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pbylowerbyte/pbylowbite pbylowerbyte/pbylowbite dtmlowerbyte/dtmbite dtmlowerbyte/dtmbite | Profibus access PBY/DTM with upper byte (big endian) deletion, use for CPC5 type 11, readback Siparrt valve PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 204 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pbyupperbyte/pbyhighbite pbyupperbyte/pbyhighbite dtmupperbyte/dtmhighbite dtmupperbyte/dtmhighbite | Profibus access PBY/DTM with lower byte (little endian) deletion, use for CPC5 type 11, readback Siparrt valve PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 205 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pby pby dtm dtm | Profibus access PBY/DTM with lower/upper byte (endian) rotation - use for Bronkhorst Flowmeter PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx DP_PA_Link_IM157.Inputs.READBACK_POS_D_CHECKBACK_SP_IN_1; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3 0; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4; Schneider FE Device IO Configuration Param10: IOType if Sipart valve (readback only): - RD_sipart | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3] Example with sipart Valve: DP_PA_Link_IM157.Inputs.READBACK_POS_D_CHECKBACK_SP_IN_1[0]
Digital Parameter | 0
Word Parameter | 0
Analog Parameter | 0
| Blue field | Schneider FE Device IO Configuration Param1: Object names
| FE_TYPE | Schneider FE Device IO Configuration Param1: If empty , it is assumed to be equivalent to 0
Param1 | oldSyntax | Schneider FE Device IO Configuration Param1: The official way to specify the address is by using Param2-4 But for old spec the syntax may be in the following form: -For FE-Type1; AI: %IWR.S.C.FOI ,AO: %IQR.S.C.FOI ,DI:%I.S.C.FOI ,DO:%Q.S.C.FOI - For Type 100-103; AI,AO: %MWxx ,AIR,AOR: %MFxx ,DI,DO: %MWxxx.y
Param2,3,4 | First address, offset,index | Schneider FE Device IO Configuration Param1: Number used to build the full address : syntax %x(F+O+I) or %x(F+O).I offset, index empty are replaced by 0, First Address is mandatory.
Param5 | Invert | Schneider FE Device IO Configuration Param1: Digital Input: When "Yes" or "y", the Hfpos is inverted before the assignment to the object.
Param6 | IOerror | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %MWxxx.y - IOObjectName (posStwill be extracted) - Empty (internal variable Name_IOERROR will be declared Default: FALSE.
Param6 | NodeStatus | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %Wwxxx.y -DI object representing the decode of the IOError (Inverted)
Param8 | Other error | Schneider FE Device IO Configuration Param1: The IOError signal is either: -When Param6 is empty it is the String Param8 -When Param6 is not empty it is a OR of the two
| OUT | Schneider FE Device IO Configuration Param1: When "out" the PosSt is send to the address (F+O+I)
Param9 | endian | Schneider FE Device IO Configuration Param1: When "endian" the Big/little Endian conversion is applied.
Param9 | RawError | Schneider FE Device IO Configuration Param1: Error in percentage of the Raw Value to generate an IOError. Ex: If Param7 = 2 with a Raw values between [0 ; 10000], if the raw value is below -200 or above 10200, an IOError is generated
Param10 | "IOType" | Schneider FE Device IO Configuration Param1: Keyword specific to hardware interface. PBY or PRM plus some references of the equipment
Note on D6: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D9: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D15: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D16: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D17: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D18: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D19: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D22: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D23: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D24: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D25: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D26: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D27: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D28: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D29: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D30: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D32: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D33: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D40: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D41: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D42: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D43: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D44: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D45: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D48: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D49: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D50: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D51: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D52: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D53: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D54: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D55: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D57: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D59: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D60: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D61: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D66: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D67: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D68: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D69: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D70: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D71: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D72: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D74: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D80: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D81: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D82: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D83: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D84: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D85: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D86: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D87: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D92: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D96: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D97: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D98: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D99: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D102: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D103: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D104: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D105: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D106: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D107: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel

## Siemens
Siemens FE Device IO Configuration
| FEType | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10 | Comment | Additional Information
Analog Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PIW300 IW300; Param9: Profinet IO station; Param10: Profibus DP Slave | Reading from periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
Analog Output | 0 | [10 empty] | No address
| 1 | Param1: Perophery address PQW300 QW300; Param9: Profinet IO station; Param10: Profibus DP Slave | Direct Address | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
Digital Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address I30.0; Param9: Profinet IO station; Param10: Profibus DP Slave | Reading from periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Reading from a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with inverted IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with IO Error
Digital Output | 0 | [10 empty] | No address
| 1 | Param1: Periphery address Q30.0; Param9: Profinet IO station; Param10: Profibus DP Slave | Writing in periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Writing in a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with inverted IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with IO Error
Analog Input Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with inverted IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with IO Error
| 201 | Param1: Periphery address PID500 ID500 | Reading from a Profibus PA valve (in Profibus DP) with 10 bytes consistency check
| 202 | Param1: Periphery address PID500 ID500 | Reading from Profibus PA sensor (in profibus DP) with 5 bytes consistency check (4 bytes for value and 1 status byte) | The IO Error evaluation is done taking into account the consistency check and the status byte
| 203 | Param1: Periphery address PID500 ID500 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | The IO Error evaluation is done taking into account the consistency check and the status byte
| 204 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation) | The IO error of this object is always set to FALSE
| 205 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | The IO Error evaluation is based on the consistency check only.
| 206 | Param1: Periphery address PID500 ID500; Param2: Address byte of the status byte PIB504 IB504 | Reading from a Profibus DP device with 4 bytes with consistency check and status byte (4 bytes for value and 1 status byte) | The IO Error evaluation is based in the status byte and the Consistency check. The status byte address shall be defined in Param2
Analog Output Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Writing in a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with inverted IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with IO Error
| 201 | Param1: Periphery address PQD500 QD500 | Writing a Profibus PA actuator in Profibus DP with 5 bytes consistency check (4 bytes for value + 1 byte for command) | The IO Error evaluation is based on the consistency check
| 205 | Param1: Periphery address PQD500 QD500 | Writing Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | The IO Error evaluation is based on the consistency check. This type shall be semected for the Bronkhorst MFC
Analog Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PID500 ID500 | Reading from periphery | No IO Error for Analog Status objects
| 100 | Param1: M address MD30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
Word Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address in byte or word format PIW300 or PIB300 IW300 or IB300 | Reading from periphery | No IO Error for Word Status objects
| 100 | Param1: M address in byte or word format MW30 or MB30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address word or byte format 40 or DBB40 | Reading from a DB without IO Error
Word Parameter | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PQW300 QW300 | Writing in periphery | No IO Error for Word Parameter objects
| 100 | Param1: M address MW30 | Writing in M area
| 101 | Param1: Address Datablock DB30; Param2: Address word 40 | Writing in a DB without IO Error

## TIA Portal
Siemens FE Device IO Configuration
| FEType | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10 | Comment | Additional Information
Analog Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PIW300 IW300; Param9: Profinet IO station; Param10: Profibus DP Slave | Reading from periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
Analog Output | 0 | [10 empty] | No address
| 1 | Param1: Perophery address PQW300 QW300; Param9: Profinet IO station; Param10: Profibus DP Slave | Direct Address | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
Digital Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address I30.0; Param9: Profinet IO station; Param10: Profibus DP Slave | Reading from periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
| 101 | Param1: Datablock bool variable Block_DB.Variable | Reading from a DB without IO Error
| 102 | Param1: Datablock bool variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Reading from a DB with inverted IO Error
| 103 | Param1: Datablock bool variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Reading from a DB with IO Error
Digital Output | 0 | [10 empty] | No address
| 1 | Param1: Periphery address Q30.0; Param9: Profinet IO station; Param10: Profibus DP Slave | Writing in periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
| 101 | Param1: Datablock bool variable Block_DB.Variable | Writing in a DB without IO Error
| 102 | Param1: Datablock bool variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Writing in a DB with inverted IO Error
| 103 | Param1: Datablock bool variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Writing in a DB with IO Error
Analog Input Real | 0 | [10 empty] | No address
| 101 | Param1: Datablock double word variable Block_DB.Variable | Reading from a DB without IO Error
| 102 | Param1: Datablock double word variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Reading from a DB with inverted IO Error
| 103 | Param1: Datablock double word variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Reading from a DB with IO Error
| 201 | Param1: Periphery address PID500 ID500 | Reading from a Profibus PA valve (in Profibus DP) with 10 bytes consistency check
| 202 | Param1: Periphery address PID500 ID500 | Reading from Profibus PA sensor (in profibus DP) with 5 bytes consistency check (4 bytes for value and 1 status byte) | The IO Error evaluation is done taking into account the consistency check and the status byte
| 203 | Param1: Periphery address PID500 ID500 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | The IO Error evaluation is done taking into account the consistency check and the status byte
| 204 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation) | The IO error of this object is always set to FALSE
| 205 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | The IO Error evaluation is based on the consistency check only.
| 206 | Param1: Periphery address PID500 ID500; Param2: Address byte of the status byte PIB504 IB504 | Reading from a Profibus DP device with 4 bytes with consistency check and status byte (4 bytes for value and 1 status byte) | The IO Error evaluation is based in the status byte and the Consistency check. The status byte address shall be defined in Param2
Analog Output Real | 0 | [10 empty] | No address
| 101 | Param1: Datablock double word variable Block_DB.Variable | Writing in a DB without IO Error
| 102 | Param1: Datablock double word variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Writing in a DB with inverted IO Error
| 103 | Param1: Datablock double word variable Block_DB.Variable; Param2: Datablock IO error variable Block_DB.Variable | Writing in a DB with IO Error
| 201 | Param1: Periphery address PQD500 QD500 | Writing a Profibus PA actuator in Profibus DP with 5 bytes consistency check (4 bytes for value + 1 byte for command) | The IO Error evaluation is based on the consistency check
| 205 | Param1: Periphery address PQD500 QD500 | Writing Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | The IO Error evaluation is based on the consistency check. This type shall be semected for the Bronkhorst MFC
Analog Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PID500 ID500 | Reading from periphery | No IO Error for Analog Status objects
| 100 | Param1: M address MD30 | Reading from M area
| 101 | Param1: Datablock double word variable Block_DB.Variable | Reading from a DB without IO Error
Word Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address in byte or word format PIW300 or PIB300 IW300 or IB300 | Reading from periphery | No IO Error for Word Status objects
| 100 | Param1: M address in byte or word format MW30 or MB30 | Reading from M area
| 101 | Param1: Datablock word or byte variable Block_DB.Variable | Reading from a DB without IO Error
Word Parameter | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PQW300 QW300 | Writing in periphery | No IO Error for Word Parameter objects
| 100 | Param1: M address MW30 | Writing in M area
| 101 | Param1: Datablock word variable Block_DB.Variable | Writing in a DB without IO Error