## Summary
|  | FEType | Global definition
0 | No address
1 | direct access to periphery
100-199 | internal access (memory ioscanning DB, etc ..)
200-299 | Fieldbus Profibus
300-399 | Fieldbus CanOpen
400-499 | Fieldbus EtherCat
Details
Step7: Siemens |  | Unity: Schneider |  | CoDeSys
FEType |  | FEType |  | FEType
0 | No address | 0 | No address | 0 | No address
1 | direct access to periphery | 1 | direct access to periphery | 1 | direct access to periphery
100 | internal memory access | 100 | internal memory access | 100 | internal memory access
101 | Read/write: DB without IO Error | 101 | Ioscanning
102 | Read/write: DB with IO Error | 102 | Ioscanning1
103 | Read/write: DB with inverted IO Error | 103 | GlobalData
|  | 104 | GlobalData1
200 |  | 200 | Read/Write Profibus
201 | Read/write: PA valve in Profibus DP | 201 | Read/Write Profibus Byte Array
202 | Read: Profibus PA sensor in Profibus DP | 202 | Read/Write Profibus word Array
203 | Read: Profibus DP device | 203 | Read/write Profibus Wago
205 | Read: Profibus Bronkhorst Mass Flow Controller | 204 | Read/write Profibus Siemens
|  | 205 | Read/write Profibus Bronkhorst
| The value redout function is the same for the FE Type 201, 202, 203 and 205. The difference between the Profibus FETypes is the IO error evaluation. Te value redout is identical | 2xx | Read/write Profibus xx
|  | 300 | CanOpen Interface
|  | 301 | Read/write CanOpenCPP_ELMB
|  |  |  | 400 | Read/Write EtherCat
Where XXX being a specifity of this product

## Schneider
Schneider FE Device IO Configuration
| FE_TYPE | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10
Analog Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel | First address | Offset | Index |  | Node Status |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 200 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
| 2xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error
Analog Input Real | 0 | [10 empty] | No address
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 200 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
| 3xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error
Analog Output | 0 | [10 empty] | No address
| 1 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 200 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
| 2xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType
Analog Output Real | 0 | [10 empty] | No address
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 2xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
Digital Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param5: Invert
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error
| 100 | OldSyntax | First address | Offset | Index | Invert | IOerror |  | Other error |  |  | Internal
| 200 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType | Fieldbus
| 201 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 202 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 2xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 3xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error
Digital Output | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param5: Invert
| 100 | OldSyntax | First address | Offset | Index | Invert | IOerror |  | Other error |  |  | Internal
| 200 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType | Fieldbus
| 201 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 202 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 2xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 3xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error
Analog Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param9: endian | Internal
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param8: OUT; Schneider FE Device IO Configuration Param9: endian
Word Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset | Internal
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param8: OUT
| 101 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 102 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 103 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 104 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 2xx | Rack.Slot.Channel | First address | Offset | Index |  | Node Status |  |  |  | IOType | Fieldbus
Digital Parameter | 0
Word Parameter | 0
Analog Parameter | 0
| Blue field | Schneider FE Device IO Configuration Param1: Object names
| FE_TYPE | Schneider FE Device IO Configuration Param1: If empty , it is assumed to be equivalent to 0
Param1 | oldSyntax | Schneider FE Device IO Configuration Param1: The official way to specify the address is by using Param2-4 But for old spec the syntax may be in the following form: -For FE-Type1; AI: %IWR.S.C.FOI ,AO: %IQR.S.C.FOI ,DI:%I.S.C.FOI ,DO:%Q.S.C.FOI - For Type 100-103; AI,AO: %MWxx ,AIR,AOR: %MFxx ,DI,DO: %MWxxx.y
Param2,3,4 | First address, offset,index | Schneider FE Device IO Configuration Param1: Number used to build the full address : syntax %x(F+O+I) or %x(F+O).I offset, index empty are replaced by 0, First Address is mandatory.
Param5 | Invert | Schneider FE Device IO Configuration Param1: When "Yes" or "y", the Hfpos is inverted before the assignment to the object.
Param6 | IOerror | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %MWxxx.y - IOObjectName (posStwill be extracted) - Empty (internal variable Name_IOERROR will be declared Default: FALSE.
Param6 | NodeStatus | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %Wwxxx.y -DI object representing the decode of the IOError (Inverted)
Param8 | Other error | Schneider FE Device IO Configuration Param1: The IOError signal is either: -When Param6 is empty it is the String Param8 -When Param6 is not empty it is a OR of the two
| OUT | Schneider FE Device IO Configuration Param1: When "out" the PosSt is send to the address (F+O+I)
Param9 | endian | Schneider FE Device IO Configuration Param1: When "endian" the Big/little Endian conversion is applied.
Param10 | "IOType" | Schneider FE Device IO Configuration Param1: Keyword specific to hardware interface. PBY or PRM plus some references of the equipment
Note on D6: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D11: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D12: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D17: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D18: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D20: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D25: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D26: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D31: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D33: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D35: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D36: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D38: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D39: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D40: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D41: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D42: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D44: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D47: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D48: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D49: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D50: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D51: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D58: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D59: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D60: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D61: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D62: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel

## Siemens
Siemens FE Device IO Configuration
| FEType | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10 | Comment
Analog Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PIW300 IW300 | Reading from periphery
Analog Output | 0 | [10 empty] | No address
| 1 | Param1: Perophery address PQW300 QW300 | Direct Address
Digital Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address I30.0 | Writing in periphery
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Reading from a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with inverted IO Error
Digital Output | 0 | [10 empty] | No address
| 1 | Param1: Periphery address Q30.0 | Writing in periphery
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Writing in a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with inverted IO Error
Analog Input Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with inverted IO Error
| 201 | Param1: Periphery address PID500 ID500 | Reading a PA valve from Profibus DP | The value redout function is the same for the FE Type 201, 202, 203 and 205. The difference between the Profibus FETypes is the IO error evaluation. Te value redout is identical
| 202 | Param1: Periphery address PID500 ID500 | Reading from Profibus PA sensor
| 203 | Param1: Periphery address PID500 ID500 | Reading from a Standard Profibus DP device
| 205 | Param1: Periphery address PID500 ID500 | Reading from a Bronkhorst Mass Flow Controller
Analog Output Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Writing in a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with inverted IO Error
| 201 | Param1: Periphery address PQD500 QD500 | Writing in a Profibus PA actuator
Analog Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PID500 ID500 | Reading from periphery
| 100 | Param1: M address MD30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
Word Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address in byte or word format PIW300 or PIB300 IW300 or IB300 | Reading from periphery
| 100 | Param1: M address in byte or word format MW30 or MB30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address word or byte format 40 or DBB40 | Reading from a DB without IO Error
Word Parameter | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PQW300 QW300 | Writing in periphery
| 100 | Param1: M address MW30 | Writing in M area
| 101 | Param1: Address Datablock DB30; Param2: Address word 40 | Writing in a DB without IO Error