## ProjectDocumentation
Project Name:
Application Name:
Project Description:
Project Owner:
Spec FAQ link: | http://cern.ch/UNICOS-SpecFAQ
Object Descriptions link: | http://cern.ch/UNICOS-ObjectDescription
Spec Changes:
Date | User | Comments | Version | HTML link

## SpecDoc
AttributeFamily | AttributeName | HelpCategory | HelpDescription
DeviceDocumentation | Description | Description | Description of the device.
DeviceDocumentation | Description | Usage | Used in the SCADA layer in the device faceplate
DeviceDocumentation | Description | DependentAttributes
DeviceDocumentation | Description | Constraints | In principle there is no limit to the number of characters used, however a long description may result in display issues at the SCADA level. Forbidden characters: ;
DeviceDocumentation | Electrical Diagram | Description | Reference to the electrical diagram in which the device is represented.
DeviceDocumentation | Electrical Diagram | Usage | Used in the SCADA layer: added to the device description in the device faceplate.
DeviceDocumentation | Electrical Diagram | DependentAttributes
DeviceDocumentation | Electrical Diagram | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
DeviceDocumentation | Remarks | Description | Field used to add relevant information about the device.
DeviceDocumentation | Remarks | Usage | This information is not used in the generation process, it remains only at the specification level for documentation purposes.
DeviceDocumentation | Remarks | DependentAttributes
DeviceDocumentation | Remarks | Constraints | Forbidden characters: ;
DeviceIdentification | Expert Name | Description | Name of the device displayed at the SCADA level. It must be unique. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
DeviceIdentification | Expert Name | Usage | It does not affect to the datapoints names in the SCADA layer.
DeviceIdentification | Expert Name | DependentAttributes | Device Links. The name of the device(s) specified in Device Links *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified in Device Links corresponds to "Name".
DeviceIdentification | Expert Name | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦] Expert Name must be unique.
DeviceIdentification | Name | Description | Name of the device. It must be unique. Max length: - Schneider: 23 - Siemens: Field objects, Controller and PCO: 19; Local: 21; otherwise: 24 Forbidden chars: [: "'@`#$%^&*?!,;=+~(){}<>¦]-., double underscore, and page break
DeviceIdentification | Name | Usage | Name displayed at the SCADA level if "Expert Name" is not specified. This name will appear in the datapoints created in the SCADA layer.
DeviceIdentification | Name | DependentAttributes | Device Links. The name of the device(s) specified in Device Links *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified in Device Links corresponds to "Name".
DeviceIdentification | Name | Constraints | Max length: - Schneider: 23 - Siemens: Field objects, Controller and PCO: 19; Local: 21; otherwise: 24 Forbidden chars: [: "'@`#$%^&*?!,;=+~(){}<>¦]-., double underscore, and page break Name must be unique.
FEDeviceAlarm | Auto Acknowledge | Description | The SCADA automatically performs the alarm acknowledge
FEDeviceAlarm | Auto Acknowledge | Usage | When TRUE, the SCADA automatically acknowledges the alarm at its occurrence. The operator doesn't have to act on this alarm.
FEDeviceAlarm | Auto Acknowledge | DependentAttributes
FEDeviceAlarm | Auto Acknowledge | Constraints | TRUE/FALSE
FEDeviceAlarm | Enable Condition | Description | Enable Condition used to enable all defined alarm thresholds (AuEXX). If blank or "logic", then condition is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT AIOBJECT.IOErrorW) is allowed.
FEDeviceAlarm | Enable Condition | Usage | Enable Condition used to enable all defined alarm thresholds (AuEXX).
FEDeviceAlarm | Enable Condition | DependentAttributes
FEDeviceAlarm | Enable Condition | Constraints | If blank or "logic", then condition is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT AIOBJECT.IOErrorW) is allowed.
FEDeviceAlarm | Multiple Types | Description | Declaration of all types of alarm in the case of a multiple dependent objects. Valid only when FEDeviceAlarm::Type is "Multiple", syntax "AlType,AlType". "AlType" must be one of the following valid alarm types: AL,FS,TS,SI.
FEDeviceAlarm | Multiple Types | Usage | Provide to the SCADA information on the Alarm types when several PCO/field objects are dependent of this Alarm
FEDeviceAlarm | Multiple Types | DependentAttributes | FEDeviceAlarm::Type
FEDeviceAlarm | Multiple Types | Constraints | Valid only when FEDeviceAlarm::Type is "Multiple", syntax "AlType,AlType" "AlType" must be one of the following valid alarm types: AL,FS,TS,SI
FEDeviceAlarm | Type | Description | Definition of the Alarm action in the Process: AL: Alarm; no interlock FS: Full Stop TS: Temporary Stop (until alarm disappears) SI: Start Interlock; block ON mode request Multiple: Several PCO/Field objects depend on Alarm - see Multiple Types.
FEDeviceAlarm | Type | Usage | There are 4 valid alarm types: AL: Alarm; will have no effect on PCO/Field FS: Full Stop; will Stop PCO/Field TS: Temporary Stop; will Stop PCO/Field until it disappears. SI: Start Interlock; will block ON mode request applied to the PCO/Field.
FEDeviceAlarm | Type | DependentAttributes | All PCO/Field object specified in this Instance If "Multiple", then must fill out Multiple Types field
FEDeviceAlarm | Type | Constraints
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | Description | Decrease speed of the set-point. Must be positive.
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | Usage
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | DependentAttributes
FEDeviceAutoRequests | Default Setpoint Speed::Decrease Speed | Constraints | Must be positive
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | Description | Increase speed of the set-point. Must be positive.
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | Usage
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | DependentAttributes
FEDeviceAutoRequests | Default Setpoint Speed::Increase Speed | Constraints | Must be positive
FEDeviceEnvironmentInputs | ClockWise Limit | Description | Hardware Feedback limit in clockwise reached
FEDeviceEnvironmentInputs | ClockWise Limit | Usage | Used to compute if the device has reached the limit in the ClockWise direction
FEDeviceEnvironmentInputs | ClockWise Limit | DependentAttributes
FEDeviceEnvironmentInputs | ClockWise Limit | Constraints | Must be a DI
FEDeviceEnvironmentInputs | CounterClockWise Limit | Description | Hardware Feedback limit in CounterClocWise reached
FEDeviceEnvironmentInputs | CounterClockWise Limit | Usage | Used to compute if the device has reached the limit in the CounterClockWise direction
FEDeviceEnvironmentInputs | CounterClockWise Limit | DependentAttributes
FEDeviceEnvironmentInputs | CounterClockWise Limit | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Feedback Analog | Description | Analog Feedback of the actuator. Must be an AI/AIR/AS.
FEDeviceEnvironmentInputs | Feedback Analog | Usage | Used to compare with the internal feedback of the device
FEDeviceEnvironmentInputs | Feedback Analog | DependentAttributes
FEDeviceEnvironmentInputs | Feedback Analog | Constraints | Must be an AI/AIR/AS
FEDeviceEnvironmentInputs | Feedback Off | Description | Feedback Off of the actuator. Must be a DI.
FEDeviceEnvironmentInputs | Feedback Off | Usage | Used to compute the "Off" status of the device
FEDeviceEnvironmentInputs | Feedback Off | DependentAttributes
FEDeviceEnvironmentInputs | Feedback Off | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Feedback On | Description | Feedback On of the actuator. Must be a DI.
FEDeviceEnvironmentInputs | Feedback On | Usage | Used to compute the "On" status of the device
FEDeviceEnvironmentInputs | Feedback On | DependentAttributes
FEDeviceEnvironmentInputs | Feedback On | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Hardware Analog Output | Description | Hardware Local Analog request to the actuator when it is in hardware local mode. Must be an AI/AIR/AS.
FEDeviceEnvironmentInputs | Hardware Analog Output | Usage | Signal able to drive the device in case of hardware local mode.
FEDeviceEnvironmentInputs | Hardware Analog Output | DependentAttributes
FEDeviceEnvironmentInputs | Hardware Analog Output | Constraints | Must be an AI/AIR/AS
FEDeviceEnvironmentInputs | Input | Description | Logic for the Alarm input signal. If blank or "logic", then input is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT DIOBJECT) is allowed.
FEDeviceEnvironmentInputs | Input | Usage | Logic for the Alarm input signal.
FEDeviceEnvironmentInputs | Input | DependentAttributes
FEDeviceEnvironmentInputs | Input | Constraints | If blank or "logic", then input is defined inside the logic. If not blank, either a single object or simplified PLC logic (e.g. RUN.X AND NOT DIOBJECT) is allowed.
FEDeviceEnvironmentInputs | Local Drive | Description | Activation of the Hardware Local Drive. Must be a DI.
FEDeviceEnvironmentInputs | Local Drive | Usage | Signal to put the actuator in Hardware Local Mode
FEDeviceEnvironmentInputs | Local Drive | DependentAttributes
FEDeviceEnvironmentInputs | Local Drive | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Local Off | Description | Local Off Request to the actuator when it is in Hardware Local Mode. Must be a DI.
FEDeviceEnvironmentInputs | Local Off | Usage | Signal to send a Local Off Request to the device
FEDeviceEnvironmentInputs | Local Off | DependentAttributes
FEDeviceEnvironmentInputs | Local Off | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Local On | Description | Local On Request to the actuator when it is in Hardware Local Mode. Must be a DI.
FEDeviceEnvironmentInputs | Local On | Usage | Signal to send a Local On Request to the device
FEDeviceEnvironmentInputs | Local On | DependentAttributes
FEDeviceEnvironmentInputs | Local On | Constraints | Must be a DI
FEDeviceEnvironmentInputs | Measured Value | Description | Process Value to be controlled. Must be an AI/AIR/AS.
FEDeviceEnvironmentInputs | Measured Value | Usage | Enter the name of sensor to be regulated
FEDeviceEnvironmentInputs | Measured Value | DependentAttributes
FEDeviceEnvironmentInputs | Measured Value | Constraints | Must be an AI/AIR/AS
FEDeviceIOConfig | FE Encoding Type | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FE Encoding Type | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FE Encoding Type | DependentAttributes | FEChannel.InterfaceParamX (where X=1-10)
FEDeviceIOConfig | FE Encoding Type | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam1 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam1 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam1 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam1 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam10 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam10 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam10 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam10 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam2 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam2 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam2 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam2 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam3 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam3 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam3 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam3 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam4 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam4 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam4 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam4 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam5 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam5 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam5 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam5 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam6 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam6 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam6 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam6 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam7 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam7 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam7 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam7 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam8 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam8 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam8 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam8 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam9 | Description | Parameter used to set up the periphery address of the device according to the various hardware module types used at the PLC level. Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam9 | Usage | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceIOConfig | FEChannel::InterfaceParam9 | DependentAttributes | FE Encoding Type
FEDeviceIOConfig | FEChannel::InterfaceParam9 | Constraints | Refer to FEEncodingType.xlsx in Specs/ folder for specific Siemens and Schneider documentation
FEDeviceManualRequests | H Warning | Description | Threshold level above which the signal produces a Warning. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | H Warning | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | H Warning | DependentAttributes
FEDeviceManualRequests | H Warning | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | HH Alarm | Description | Threshold level above which the signal produces an Alarm. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | HH Alarm | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | HH Alarm | DependentAttributes
FEDeviceManualRequests | HH Alarm | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | L Warning | Description | Threshold level below which the signal produces a Warning. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | L Warning | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | L Warning | DependentAttributes
FEDeviceManualRequests | L Warning | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | LL Alarm | Description | Threshold level below which the signal produces an Alarm. Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL).
FEDeviceManualRequests | LL Alarm | Usage | 5 types of encoding - A number: operator can change it - An object (AS,APAR,AIR) - A keyword "logic": process logic will assign a value to this signal. - Simplified PLC logic, e.g. OBJECT + 2 - An empty field: no alarm
FEDeviceManualRequests | LL Alarm | DependentAttributes
FEDeviceManualRequests | LL Alarm | Constraints | Can be a number, an object (AS,APAR,AIR), keyword "logic", simplified PLC logic (e.g. OBJECT + 2), or empty (no alarm). All defined thresholds must be ordered (HH>H>L>LL)
FEDeviceManualRequests | Parameter Limit Off/Closed | Description | Limit below which the actuator status is "Off". Must be between Range Min and Range Max.
FEDeviceManualRequests | Parameter Limit Off/Closed | Usage | Used to compute the "Off" status of the device corresponding to the widget being empty in SCADA.
FEDeviceManualRequests | Parameter Limit Off/Closed | DependentAttributes
FEDeviceManualRequests | Parameter Limit Off/Closed | Constraints | Must be between Range Min and Range Max
FEDeviceManualRequests | Parameter Limit On/Open | Description | Limit above which the actuator status is "On". Must be between Range Min and Range Max.
FEDeviceManualRequests | Parameter Limit On/Open | Usage | Used to compute the "On" status of the device corresponding to the widget being completely filled in SCADA.
FEDeviceManualRequests | Parameter Limit On/Open | DependentAttributes
FEDeviceManualRequests | Parameter Limit On/Open | Constraints | Must be between Range Min and Range Max
FEDeviceOutputs | Analog Process Output | Description | Analog Output connected to the process. Must be an AO or AS.
FEDeviceOutputs | Analog Process Output | Usage
FEDeviceOutputs | Analog Process Output | DependentAttributes
FEDeviceOutputs | Analog Process Output | Constraints | Must be an AO or AS
FEDeviceOutputs | ClockWise to Reference Switch | Description | Use the ClockWise LimitSwitch as a Reference Switch. Must be a DO.
FEDeviceOutputs | ClockWise to Reference Switch | Usage | Use the ClockWise Limit Switch as a Reference Switch in old equipment that don't allow to do it directly.
FEDeviceOutputs | ClockWise to Reference Switch | DependentAttributes
FEDeviceOutputs | ClockWise to Reference Switch | Constraints | Must be a DO.
FEDeviceOutputs | Controlled Objects | Description | List of devices to be controlled Must be Analog/Anadig/AnaDO/MFC/Controller
FEDeviceOutputs | Controlled Objects | Usage | Enter name of device to be controlled. If several, separate device names with commas.
FEDeviceOutputs | Controlled Objects | DependentAttributes
FEDeviceOutputs | Controlled Objects | Constraints | Must be Analog/Anadig/AnaDO/MFC/Controller
FEDeviceOutputs | Digital Process Output | Description | Output connected to the process. Must be a DO.
FEDeviceOutputs | Digital Process Output | Usage
FEDeviceOutputs | Digital Process Output | DependentAttributes
FEDeviceOutputs | Digital Process Output | Constraints | Must be a DO
FEDeviceOutputs | Driver Enable | Description | Enables the external Power Unit Driver for the motor.
FEDeviceOutputs | Driver Enable | Usage | Used to power off/on the Driver for doing the reference search without moving.
FEDeviceOutputs | Driver Enable | DependentAttributes
FEDeviceOutputs | Driver Enable | Constraints | Must be a DO.
FEDeviceOutputs | Output Off | Description | Negative Output connected to the process for the Bipolar PWM. Must be a DO.
FEDeviceOutputs | Output Off | Usage
FEDeviceOutputs | Output Off | DependentAttributes | Bipolar PWM must be selected as PWM Mode
FEDeviceOutputs | Output Off | Constraints | Must be a DO
FEDeviceOutputs | Output On | Description | Digital Output connected to the process for the Classic PWM. Positive Output connected to the process for the Bipolar PWM. Must be a DO.
FEDeviceOutputs | Output On | Usage
FEDeviceOutputs | Output On | DependentAttributes
FEDeviceOutputs | Output On | Constraints | Must be a DO
FEDeviceOutputs | Process Output | Description | Output connected to the process. Must be a DO.
FEDeviceOutputs | Process Output | Usage
FEDeviceOutputs | Process Output | DependentAttributes
FEDeviceOutputs | Process Output | Constraints | Must be a DO
FEDeviceOutputs | Process Output Off | Description | Output Off connected to the process. Must be a DO.
FEDeviceOutputs | Process Output Off | Usage | Used when the actuator is driven by 2 DO. Some actuators (rare) have 1 DO to open and 1 DO to close (bistable behavior). This DO closes the device.
FEDeviceOutputs | Process Output Off | DependentAttributes | Process Output must be filled
FEDeviceOutputs | Process Output Off | Constraints | Must be a DO
FEDeviceOutputs | Simulated Reference Switch | Description | Simulate Reference Switch. Must be a DO.
FEDeviceOutputs | Simulated Reference Switch | Usage | Used to simulate Reference Switch in equipment that doesn't have it.
FEDeviceOutputs | Simulated Reference Switch | DependentAttributes
FEDeviceOutputs | Simulated Reference Switch | Constraints | Must be a DO.
FEDeviceOutputs | Valve Order | Description | OnOff object representing a valve located in front of the device. Must be a declared OnOff object.
FEDeviceOutputs | Valve Order | Usage | This valve will be driven by the MFC. It prevents leaks because the MFC cannot be fully hermetic when at minimum flow or closed.
FEDeviceOutputs | Valve Order | DependentAttributes | See corresponding OnOff device
FEDeviceOutputs | Valve Order | Constraints | Must be a declared OnOff object
FEDeviceParameters | Alarm Delay (s) | Description | Time delay applied to the condition that sets an Alarm. Can be a number (>= 0), an object (AS,APAR), or empty (set to 0 by default). If = 0, then no delay.
FEDeviceParameters | Alarm Delay (s) | Usage | Active alarm of a duration lower than this delay are ignored. Filter on spikes in Alarm condition.
FEDeviceParameters | Alarm Delay (s) | DependentAttributes
FEDeviceParameters | Alarm Delay (s) | Constraints | Can be a number (>= 0), an object (AS,APAR), or empty (set to 0 by default). If = 0, then no delay.
FEDeviceParameters | CC0 Max Flow (Unit/time) | Description | Device maximum flow (when fully open) with the fluid corresponding to calibration curve 0. Unit/time defined by the operator. Cannot be null/empty (there must be at least one fluid).
FEDeviceParameters | CC0 Max Flow (Unit/time) | Usage
FEDeviceParameters | CC0 Max Flow (Unit/time) | DependentAttributes
FEDeviceParameters | CC0 Max Flow (Unit/time) | Constraints | Cannot be null/empty (there must be at least one fluid)
FEDeviceParameters | CC1 Max Flow (Unit/time) | Description | Device maximum flow (when fully open) with the fluid corresponding to calibration curve 0. Unit/time defined by the operator. Can be null/empty.
FEDeviceParameters | CC1 Max Flow (Unit/time) | Usage
FEDeviceParameters | CC1 Max Flow (Unit/time) | DependentAttributes
FEDeviceParameters | CC1 Max Flow (Unit/time) | Constraints | Can be null/empty.
FEDeviceParameters | CC2 Max Flow (Unit/time) | Description | Device maximum flow (when fully open) with the fluid corresponding to calibration curve 0. Unit/time defined by the operator. Can be null/empty.
FEDeviceParameters | CC2 Max Flow (Unit/time) | Usage
FEDeviceParameters | CC2 Max Flow (Unit/time) | DependentAttributes
FEDeviceParameters | CC2 Max Flow (Unit/time) | Constraints | Can be null/empty.
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | Description | Time constant of the 1st order filter applied to the Measured Value. Must be larger than the PLC cycle time.
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | Usage | The time filter is applied on the measured value to reduce noise
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | DependentAttributes
FEDeviceParameters | Controller Parameters::MV Filter Time (s) | Constraints | Must be larger than the PLC cycle time
FEDeviceParameters | Controller Parameters::Output Range Max | Description | Output Range Max if different from controlled devices. If empty, take range of the first controlled device.
FEDeviceParameters | Controller Parameters::Output Range Max | Usage | Can be used if split range is performed with the controller
FEDeviceParameters | Controller Parameters::Output Range Max | DependentAttributes
FEDeviceParameters | Controller Parameters::Output Range Max | Constraints
FEDeviceParameters | Controller Parameters::Output Range Min | Description | Output Range Min if different from controlled devices. If empty, take range of the first controlled device.
FEDeviceParameters | Controller Parameters::Output Range Min | Usage | Can be used if split range is performed with the controller
FEDeviceParameters | Controller Parameters::Output Range Min | DependentAttributes
FEDeviceParameters | Controller Parameters::Output Range Min | Constraints
FEDeviceParameters | Controller Parameters::PID Cycle (s) | Description | Cycle time to call the PID algorithm. Must be larger than the PLC cycle time.
FEDeviceParameters | Controller Parameters::PID Cycle (s) | Usage
FEDeviceParameters | Controller Parameters::PID Cycle (s) | DependentAttributes
FEDeviceParameters | Controller Parameters::PID Cycle (s) | Constraints | Must be larger than the PLC cycle time
FEDeviceParameters | Controller Parameters::RA | Description | Reverse Action on the controller
FEDeviceParameters | Controller Parameters::RA | Usage | If TRUE, the Kc parameter will be negative, i.e. if MV > SP, Output will increase. If FALSE (=default), Kc will be positive, i.e. if MV > SP, Output will decrease.
FEDeviceParameters | Controller Parameters::RA | DependentAttributes
FEDeviceParameters | Controller Parameters::RA | Constraints
FEDeviceParameters | Controller Parameters::Scaling Method | Description | Scaling method applied to the PID
FEDeviceParameters | Controller Parameters::Scaling Method | Usage | Input Scaling (1, default): the SP and the MV are scaled. Output 0-100% Input/Output Scaling (2): Same as Input Scaling but Output can be scaled to engineering values (Output Range Min/Max) No Scaling (3): use engineering values. Kc has physical meaning
FEDeviceParameters | Controller Parameters::Scaling Method | DependentAttributes
FEDeviceParameters | Controller Parameters::Scaling Method | Constraints
FEDeviceParameters | Deadband (%) | Description | Deadband applied to the Engineering value at the PLC level.
FEDeviceParameters | Deadband (%) | Usage | The value entered here must be consistent with the resolution of the PLC channel.
FEDeviceParameters | Deadband (%) | DependentAttributes
FEDeviceParameters | Deadband (%) | Constraints | Variations of the Engineering value below the % of the Engineering range will be discarded.
FEDeviceParameters | Deadband Trigger | Description | Deadband value in engineering units to Trigger a new Positioning job
FEDeviceParameters | Deadband Trigger | Usage | Minimum difference between the Actual position and the Commanded position to trigger a new positioning job.
FEDeviceParameters | Deadband Trigger | DependentAttributes
FEDeviceParameters | Deadband Trigger | Constraints | Must be positive
FEDeviceParameters | Default Value | Description | Default value for the parameter
FEDeviceParameters | Default Value | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Value | DependentAttributes
FEDeviceParameters | Default Value | Constraints
FEDeviceParameters | Encoder Type | Description | Type of encoder in use.
FEDeviceParameters | Encoder Type | Usage | Here you can choose between different encoder types.
FEDeviceParameters | Encoder Type | DependentAttributes
FEDeviceParameters | Encoder Type | Constraints
FEDeviceParameters | Filtering Time (s) | Description | First Order Filter applied to the Engineering value at the PLC level.
FEDeviceParameters | Filtering Time (s) | Usage | A first order filter is applied to the engineering value.
FEDeviceParameters | Filtering Time (s) | DependentAttributes
FEDeviceParameters | Filtering Time (s) | Constraints | the filter will absorb the noise of the signal
FEDeviceParameters | Flow Conversion | Description | Scale factor to convert set point and flow values to different units, for display and control purposes. Use this factor when the device works in one physical unit (e.g. l/min) but the operator wants to view in another unit (e.g. l/h)
FEDeviceParameters | Flow Conversion | Usage
FEDeviceParameters | Flow Conversion | DependentAttributes
FEDeviceParameters | Flow Conversion | Constraints | Must be > 0
FEDeviceParameters | Manual Decrease Speed (Unit/s) | Description | Decrease speed of the actuator when user requests a new value from SCADA. Must be positive.
FEDeviceParameters | Manual Decrease Speed (Unit/s) | Usage
FEDeviceParameters | Manual Decrease Speed (Unit/s) | DependentAttributes
FEDeviceParameters | Manual Decrease Speed (Unit/s) | Constraints | Must be positive
FEDeviceParameters | Manual Decrease Step (Unit) | Description | Step amplitude in Unit value when user requests a "decrease value" from SCADA. Must be positive and < (Range Max-Range Min)
FEDeviceParameters | Manual Decrease Step (Unit) | Usage
FEDeviceParameters | Manual Decrease Step (Unit) | DependentAttributes
FEDeviceParameters | Manual Decrease Step (Unit) | Constraints | Must be positive and < (Range Max-Range Min)
FEDeviceParameters | Manual Increase Speed (Unit/s) | Description | Increase speed of the actuator when user requests a new value from SCADA. Must be positive.
FEDeviceParameters | Manual Increase Speed (Unit/s) | Usage
FEDeviceParameters | Manual Increase Speed (Unit/s) | DependentAttributes
FEDeviceParameters | Manual Increase Speed (Unit/s) | Constraints | Must be positive
FEDeviceParameters | Manual Increase Step (Unit) | Description | Step amplitude in Unit value when user requests an "increase value" from SCADA. Must be positive and < (Range Max-Range Min).
FEDeviceParameters | Manual Increase Step (Unit) | Usage
FEDeviceParameters | Manual Increase Step (Unit) | DependentAttributes
FEDeviceParameters | Manual Increase Step (Unit) | Constraints | Must be positive and < (Range Max-Range Min)
FEDeviceParameters | Max Speed | Description | Maximum speed allowed. It has to be between 1 and 254
FEDeviceParameters | Max Speed | Usage | Specifies the maximum speed that the device can move safely.
FEDeviceParameters | Max Speed | DependentAttributes
FEDeviceParameters | Max Speed | Constraints | Must be less than 254
FEDeviceParameters | Maximum Range | Description | Highest Position that the device can reach.
FEDeviceParameters | Maximum Range | Usage | Highest Position that the device can reach.
FEDeviceParameters | Maximum Range | DependentAttributes
FEDeviceParameters | Maximum Range | Constraints | Must be bigger than Minimum Range.
FEDeviceParameters | Minimum Range | Description | Lowest Position that the device can reach.
FEDeviceParameters | Minimum Range | Usage | Lowest position that the device can reach.
FEDeviceParameters | Minimum Range | DependentAttributes
FEDeviceParameters | Minimum Range | Constraints
FEDeviceParameters | Offset | Description | Offset added in engineering units for the conversion between steps and engineering units.
FEDeviceParameters | Offset | Usage
FEDeviceParameters | Offset | DependentAttributes
FEDeviceParameters | Offset | Constraints | Must be positive
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 1 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 2 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 3 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 4 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 5 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 6 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 7 Allowance | Constraints
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | Description | Allow the transition from one option mode to another when the PCO is running. String of 8 Booleans (0/1) to define if transition is allowed to other option modes.
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | Usage
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | DependentAttributes
FEDeviceParameters | Option Mode Allowance Table::Option Mode 8 Allowance | Constraints
FEDeviceParameters | PWM Parameters::Max Deviation | Description | Maximum amplitude of the PWM output corresponding to a duty cycle of 100% (the 'DO On' remains at One). Must be between Range Min and Range Max.
FEDeviceParameters | PWM Parameters::Max Deviation | Usage
FEDeviceParameters | PWM Parameters::Max Deviation | DependentAttributes
FEDeviceParameters | PWM Parameters::Max Deviation | Constraints | Must be between Range Min and Range Max
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | Description | Minimum pulse duration of the PWM. Must be larger than the PLC cycle time.
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | Usage
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | DependentAttributes
FEDeviceParameters | PWM Parameters::Minimum Duration (s) | Constraints | Must be larger than the PLC cycle time
FEDeviceParameters | PWM Parameters::Time Period (s) | Description | Time Period to generate the Pulse Wave Modulation (PWM). The time period must be larger than the PLC cycle time and larger than the pulse minimum duration.
FEDeviceParameters | PWM Parameters::Time Period (s) | Usage
FEDeviceParameters | PWM Parameters::Time Period (s) | DependentAttributes | PWM Parameters.Minimum Duration (s)
FEDeviceParameters | PWM Parameters::Time Period (s) | Constraints | The time period must be larger than the PLC cycle time and larger than the pulse minimum duration
FEDeviceParameters | ParReg::Constant Time Pulse | Description | Only relevant if object is pulsed (Pulse Duration (s) column is not blank): - if blank/FALSE: output is pulsed until feedback is received - if TRUE: output will always pulse for specified duration, regardless of the feedback
FEDeviceParameters | ParReg::Constant Time Pulse | Usage
FEDeviceParameters | ParReg::Constant Time Pulse | DependentAttributes | Pulse Duration (s)
FEDeviceParameters | ParReg::Constant Time Pulse | Constraints | Only taken into account if Pulse Duration (s) is not blank
FEDeviceParameters | ParReg::Convert ratio to Unit/time | Description | Set this flag to TRUE if the hardware reads flow as a ratio (%) of max flow. If TRUE, all set point and flow values will be converted from % into physical units using the max flow defined in "CCn Max Flow (Unit/time)" attribute.
FEDeviceParameters | ParReg::Convert ratio to Unit/time | Usage
FEDeviceParameters | ParReg::Convert ratio to Unit/time | DependentAttributes | CCn Max Flow (Unit/time)
FEDeviceParameters | ParReg::Convert ratio to Unit/time | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Fail-Safe | Description | Fail Safe position of the actuator
FEDeviceParameters | ParReg::Fail-Safe | Usage | This is the position of the device in case of interlock.
FEDeviceParameters | ParReg::Fail-Safe | DependentAttributes
FEDeviceParameters | ParReg::Fail-Safe | Constraints
FEDeviceParameters | ParReg::Feedback | Description | Enables the use of the Analog Feedback from the potentiometer as Support for positioning, but still open loop.
FEDeviceParameters | ParReg::Feedback | Usage | Activate this option to use the Feedback from the potentiometer as support instead of defining position.
FEDeviceParameters | ParReg::Feedback | DependentAttributes
FEDeviceParameters | ParReg::Feedback | Constraints
FEDeviceParameters | ParReg::Feedback Off | Description | The hardware device does not provide feedback signals. If TRUE, all feedback signals from the hardware will be simulated.
FEDeviceParameters | ParReg::Feedback Off | Usage
FEDeviceParameters | ParReg::Feedback Off | DependentAttributes
FEDeviceParameters | ParReg::Feedback Off | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Full/Empty Animation | Description | Full/Empty Widget Animation type: If Full/Empty, the object is always animated full/empty if active Feedback Off/On is not set. Otherwise, if Full/Half/Empty, the object is only animated half full. For more details, see OnOff object description
FEDeviceParameters | ParReg::Full/Empty Animation | Usage | To always represent the widget as Full or Empty when only one Hardware Feedback is declared.
FEDeviceParameters | ParReg::Full/Empty Animation | DependentAttributes
FEDeviceParameters | ParReg::Full/Empty Animation | Constraints | Full/Empty Animation is applied, when only one Hardware Feedback is declared (PHFOn or PHFOff).
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | Description | The operator cannot act on the control of the Flow totalizer. If TRUE, the flow totalizer is only managed by the process.
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | Usage
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | DependentAttributes
FEDeviceParameters | ParReg::Inhibit Totalizer cmd | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Description | Strategy to adopt to restart the device after a Full Stop Interlock.
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Usage | FALSE: Device restarts after acknowledge. TRUE only if Full Stop disappeared: Ack+Allow Restart needed (possible only if FS disappeared) TRUE even if Full Stop still active: Ack+Allow Restart needed (possible at any moment)
FEDeviceParameters | ParReg::Manual Restart after Full Stop | DependentAttributes
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Constraints | All devices of the application should have the same "Manual Restart after Full Stop"
FEDeviceParameters | ParReg::Noise Filter | Description | Remove noisy flow measurements for low flow set points. If TRUE noisy flow measurements (< 0.1% of the Max flow) will be suppressed when the valve setpoint is Min or closed.
FEDeviceParameters | ParReg::Noise Filter | Usage
FEDeviceParameters | ParReg::Noise Filter | DependentAttributes | CCn Max Flow (Unit/time)
FEDeviceParameters | ParReg::Noise Filter | Constraints | TRUE/FALSE
FEDeviceParameters | ParReg::Outputs Maintained | Description | Maintain the output when Range Max is reached.
FEDeviceParameters | ParReg::Outputs Maintained | Usage | TRUE: The process output will remain TRUE when the Range Max is reached. FALSE: The process output will go FALSE when the Range Max is reached.
FEDeviceParameters | ParReg::Outputs Maintained | DependentAttributes
FEDeviceParameters | ParReg::Outputs Maintained | Constraints
FEDeviceParameters | ParReg::PWM Mode | Description | Mode used to generate the Pulse Wave Modulation (PWM).
FEDeviceParameters | ParReg::PWM Mode | Usage | Classic mode uses a single DO. Bipolar mode uses 2 DO (1 DO to go up and 1 DO to go down).
FEDeviceParameters | ParReg::PWM Mode | DependentAttributes | If Bipolar mode is selected, the field "Output Off" must be specified
FEDeviceParameters | ParReg::PWM Mode | Constraints
FEDeviceParameters | ParReg::Position Alarm | Description | If TRUE, set Position Alarm if a Local object has no hardware feedback from its only active feedback signal
FEDeviceParameters | ParReg::Position Alarm | Usage | Position Alarm will display SCADA widget in red in this case and allow user to quickly identify valves which are not in correct position
FEDeviceParameters | ParReg::Position Alarm | DependentAttributes
FEDeviceParameters | ParReg::Position Alarm | Constraints | Position Alarm Animation is applied, when only one Hardware Feedback is declared (PHFOn or PHFOff).
FEDeviceParameters | ParReg::Switches Configuration | Description | Enables the activation of the Feedback ClockWise and CounterClockWise of the object via a hardware sensor connected to the stepper module.
FEDeviceParameters | ParReg::Switches Configuration | Usage | This describes the switches configuration in the physical installation.
FEDeviceParameters | ParReg::Switches Configuration | DependentAttributes
FEDeviceParameters | ParReg::Switches Configuration | Constraints
FEDeviceParameters | Pulse Duration (s) | Description | Pulse duration (s). - if != 0, OnOff output will be pulsed for X seconds. - if blank or =0, output is not pulsed. N.B. Pulse behaviour depends on "Constant Time Pulse" column.
FEDeviceParameters | Pulse Duration (s) | Usage | Determines whether OnOff object is pulsed or not
FEDeviceParameters | Pulse Duration (s) | DependentAttributes | Constant Time Pulse
FEDeviceParameters | Pulse Duration (s) | Constraints
FEDeviceParameters | Range Max | Description | Maximum engineering value of the device.
FEDeviceParameters | Range Max | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Range Max | DependentAttributes
FEDeviceParameters | Range Max | Constraints | The value specified here must be consistent with the format defined in the field "Format".
FEDeviceParameters | Range Min | Description | Minimum engineering value of the device.
FEDeviceParameters | Range Min | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Range Min | DependentAttributes
FEDeviceParameters | Range Min | Constraints | The value specified here must be consistent with the format defined in the field "Format".
FEDeviceParameters | Raw Max | Description | Minimum raw value of the device.
FEDeviceParameters | Raw Max | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Raw Max | DependentAttributes
FEDeviceParameters | Raw Max | Constraints
FEDeviceParameters | Raw Min | Description | Minimum raw value of the device.
FEDeviceParameters | Raw Min | Usage | A linear conversion is performed between the raw range and engineering range.
FEDeviceParameters | Raw Min | DependentAttributes
FEDeviceParameters | Raw Min | Constraints
FEDeviceParameters | Reference Position | Description | Position of the Reference Switch in engineering units referenced to the Minimum and Maximum Position.
FEDeviceParameters | Reference Position | Usage | Position of the device after finishing the reference search.
FEDeviceParameters | Reference Position | DependentAttributes
FEDeviceParameters | Reference Position | Constraints
FEDeviceParameters | Scale | Description | Number of Steps to move for one engineering unit.
FEDeviceParameters | Scale | Usage | To calculate the number of steps that the motor will move, the distance is multiplied by this number.
FEDeviceParameters | Scale | DependentAttributes
FEDeviceParameters | Scale | Constraints | Must be positive
FEDeviceParameters | Volume Conversion | Description | Scale factor to convert measured volume to different units. Use this factor when the device works in one physical unit (e.g. l) but the operator wants to view in another unit (e.g. m3). Value 0 should not be applied.
FEDeviceParameters | Volume Conversion | Usage
FEDeviceParameters | Volume Conversion | DependentAttributes
FEDeviceParameters | Volume Conversion | Constraints | Value 0 should not be applied.
FEDeviceParameters | Warning Deadband Value (Unit) | Description | Deadband value to compute the position warning of the device (Discordance). Must be positive.
FEDeviceParameters | Warning Deadband Value (Unit) | Usage | can be a positive number or a parameter
FEDeviceParameters | Warning Deadband Value (Unit) | DependentAttributes
FEDeviceParameters | Warning Deadband Value (Unit) | Constraints | Must be positive
FEDeviceParameters | Warning Time Delay (s) | Description | Delay applied to the Position Alarm when there is a discordance between OutputOrder and Feedback position. Must be positive.
FEDeviceParameters | Warning Time Delay (s) | Usage | can be a positive number or a parameter
FEDeviceParameters | Warning Time Delay (s) | DependentAttributes
FEDeviceParameters | Warning Time Delay (s) | Constraints | Must be positive
FEDeviceVariables | Default PID Parameters::Kc | Description | Default Kc parameter (Gain) of the Controller at the initialization of the PLC. Must be positive. If reverse action, put TRUE in the "Reverse Action" field. If blank, will be set to 1.0 by default.
FEDeviceVariables | Default PID Parameters::Kc | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Kc | DependentAttributes
FEDeviceVariables | Default PID Parameters::Kc | Constraints | Must be positive. If reverse action, put TRUE in the "Reverse Action" field. If blank, will be set to 1.0 by default.
FEDeviceVariables | Default PID Parameters::Out High Limit | Description | Default High Limit for the Controller output at the initialization of the PLC. Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Max.
FEDeviceVariables | Default PID Parameters::Out High Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Out High Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::Out High Limit | Constraints | Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Max
FEDeviceVariables | Default PID Parameters::Out Low Limit | Description | Default Low Limit for the Controller output at the initialization of the PLC. Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Min.
FEDeviceVariables | Default PID Parameters::Out Low Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Out Low Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::Out Low Limit | Constraints | Must be between Output Range Min and Output Range Max of the controlled device. If blank, will be set to Output Range Min
FEDeviceVariables | Default PID Parameters::SP High Limit | Description | Default High Limit for the Controller Set-Point at the initialization of the PLC. Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Max of the MV.
FEDeviceVariables | Default PID Parameters::SP High Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::SP High Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::SP High Limit | Constraints | Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Max of the MV
FEDeviceVariables | Default PID Parameters::SP Low Limit | Description | Default Low Limit for the Controller Set-Point at the initialization of the PLC. Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Min of the MV.
FEDeviceVariables | Default PID Parameters::SP Low Limit | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::SP Low Limit | DependentAttributes
FEDeviceVariables | Default PID Parameters::SP Low Limit | Constraints | Must be between Range Min and Range Max of the Measured Value (MV). If blank, will be set to Range Min of the MV
FEDeviceVariables | Default PID Parameters::Setpoint | Description | Default Set-Point of the Controller at the initialization of the PLC. Must be between Range Min and Range Max of the Measured Value. If blank, will be set to 0.0 by default.
FEDeviceVariables | Default PID Parameters::Setpoint | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Setpoint | DependentAttributes
FEDeviceVariables | Default PID Parameters::Setpoint | Constraints | Must be between Range Min and Range Max of the Measured Value. If blank, will be set to 0.0 by default.
FEDeviceVariables | Default PID Parameters::Td | Description | Default Td parameter (Derivative Time) of the Controller at the initialization of the PLC. Must be >= 0. If = 0, then derivative component is removed. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Td | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Td | DependentAttributes
FEDeviceVariables | Default PID Parameters::Td | Constraints | Must be >= 0. If = 0, then derivative component is removed. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Tds | Description | Default Tds parameter (time constant of the 1st order filter on the derivative term) of the Controller at the initialization of the PLC. Must be >= 0. If = 0, then no filtering of the derivative term. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Tds | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Tds | DependentAttributes
FEDeviceVariables | Default PID Parameters::Tds | Constraints | Must be >= 0. If = 0, then no filtering of the derivative term. If blank, will be set to 0.0s by default.
FEDeviceVariables | Default PID Parameters::Ti | Description | Default Ti parameter (Integration Time) of the Controller at the initialization of the PLC. Must be >= 0. If = 0, then integral component is removed. If blank, will be set to 100.0s by default.
FEDeviceVariables | Default PID Parameters::Ti | Usage | can be a positive number or a parameter
FEDeviceVariables | Default PID Parameters::Ti | DependentAttributes
FEDeviceVariables | Default PID Parameters::Ti | Constraints | Must be >= 0. If = 0, then integral component is removed. If blank, will be set to 100.0s by default.
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicSections::BL User Template | Description | Define user template for the Basic Logic
LogicDeviceDefinitions | CustomLogicSections::BL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::BL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::BL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | Description | Define user template for the Common Dependent Object Logic
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::CDOL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::CL User Template | Description | Define user template for the Configuration Logic
LogicDeviceDefinitions | CustomLogicSections::CL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::CL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::CL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Description | Define user template for the Dependent Logic
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::DL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::GL User Template | Description | Define user template for the Global Logic
LogicDeviceDefinitions | CustomLogicSections::GL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::GL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::GL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::IL User Template | Description | Define user template for the Interlock Logic
LogicDeviceDefinitions | CustomLogicSections::IL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::IL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::IL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::INST User Template | Description | Define user template for the instantiation of the PCO
LogicDeviceDefinitions | CustomLogicSections::INST User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::INST User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::INST User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::SL User Template | Description | Define user template for the Sequencer Logic
LogicDeviceDefinitions | CustomLogicSections::SL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::SL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::SL User Template | Constraints
LogicDeviceDefinitions | CustomLogicSections::TL User Template | Description | Define user template for the Transition Logic
LogicDeviceDefinitions | CustomLogicSections::TL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::TL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::TL User Template | Constraints
LogicDeviceDefinitions | External Master | Description | Master of the device if located in another PLC for WinCCOA.
LogicDeviceDefinitions | External Master | Usage | The external master will give automatic requests to the device from another PLC. To be specified only if master is empty.
LogicDeviceDefinitions | External Master | DependentAttributes
LogicDeviceDefinitions | External Master | Constraints | Must be a single PCO for field objects, controller, or PCO.
LogicDeviceDefinitions | Master | Description | Master of the device (relative to the hierarchy of dependent objects).
LogicDeviceDefinitions | Master | Usage | The master will give automatic requests to the device. The master object will appear in the list of "Device Links" in the device right-click menu.
LogicDeviceDefinitions | Master | DependentAttributes
LogicDeviceDefinitions | Master | Constraints | Must be a single PCO for field objects, controller, or PCO. Must be PCO or field objects for alarms (several masters are allowed in the case of multiple alarms, separated by commas or spaces).
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Description | The SCADA automatically performs the alarm acknowledge
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Usage | When TRUE, the SCADA automatically acknowledges the alarm at its occurrence. The operator doesn't have to act on this alarm.
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | DependentAttributes
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Constraints | TRUE/FALSE
SCADADeviceAlarms | Alarm Config::Level | Description | Classification of the importance of the Alarm
SCADADeviceAlarms | Alarm Config::Level | Usage | Level 0: Information Level 1: Warning Level 2: Alarm Level 3: Safety Alarm
SCADADeviceAlarms | Alarm Config::Level | DependentAttributes
SCADADeviceAlarms | Alarm Config::Level | Constraints
SCADADeviceAlarms | Alarm Config::Masked | Description | Alarm signal is ignored by the SCADA
SCADADeviceAlarms | Alarm Config::Masked | Usage | When TRUE, the Alarm signal is not recorded into the ALARM database
SCADADeviceAlarms | Alarm Config::Masked | DependentAttributes
SCADADeviceAlarms | Alarm Config::Masked | Constraints | TRUE/FALSE
SCADADeviceAlarms | Alarm Config::SMS Category | Description | This Alarm message will follow rules defined in the corresponding SMS User Group (comma-separated list)
SCADADeviceAlarms | Alarm Config::SMS Category | Usage | Defines a specific treatment for each SMS message
SCADADeviceAlarms | Alarm Config::SMS Category | DependentAttributes
SCADADeviceAlarms | Alarm Config::SMS Category | Constraints | The name must correspond to the SMS user group (unProcessAlarm,...)
SCADADeviceAlarms | Analog Thresholds::H Warning | Description | High (H) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::H Warning | Usage | Used to define an H Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::H Warning | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::H Warning | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Description | High High (HH) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Usage | Used to define an HH Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::HH Alarm | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::L Warning | Description | Low (L) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::L Warning | Usage | Used to define an L Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::L Warning | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::L Warning | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Description | Low Low (LL) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Usage | Used to define an LL Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::LL Alarm | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Binary State::Alarm On State | Description | State of the device where the PVSS alert should be triggered. Blank/empty (=default) indicates that there is no PVSS alert.
SCADADeviceAlarms | Binary State::Alarm On State | Usage | This alarm is only used at SCADA level for information and It has no impact on the process.
SCADADeviceAlarms | Binary State::Alarm On State | DependentAttributes
SCADADeviceAlarms | Binary State::Alarm On State | Constraints
SCADADeviceAlarms | Message | Description | Message to display when alarm is set in SCADA
SCADADeviceAlarms | Message | Usage | The message specified here will be displayed in the Alarm List
SCADADeviceAlarms | Message | DependentAttributes
SCADADeviceAlarms | Message | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[:"'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Analog Archive | Description | Name of the analog archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Analog Archive | Usage | The analog values of the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Analog Archive | DependentAttributes
SCADADeviceDataArchiving | Analog Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Archive Mode | Constraints
SCADADeviceDataArchiving | Boolean Archive | Description | Name of the Boolean archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Boolean Archive | Usage | The boolean values of the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Boolean Archive | DependentAttributes
SCADADeviceDataArchiving | Boolean Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the engineering values of the object
SCADADeviceDataArchiving | Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Deadband Type | Constraints
SCADADeviceDataArchiving | Deadband Value | Description | Deadband value for the SCADA archiving of the engineering values of the object Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Deadband Value | Usage
SCADADeviceDataArchiving | Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Event Archive | Description | Name of the event archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Event Archive | Usage | The events generated by the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Event Archive | DependentAttributes
SCADADeviceDataArchiving | Event Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Flow::Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Flow::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Flow::Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Flow::Archive Mode | Constraints
SCADADeviceDataArchiving | Flow::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the Flow.
SCADADeviceDataArchiving | Flow::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Flow::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Flow::Deadband Type | Constraints
SCADADeviceDataArchiving | Flow::Deadband Value | Description | Deadband value for the SCADA archiving of the Flow. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Flow::Deadband Value | Usage
SCADADeviceDataArchiving | Flow::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Flow::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Flow::Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object. Must be positive.
SCADADeviceDataArchiving | Flow::Time Filter (s) | Usage
SCADADeviceDataArchiving | Flow::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Flow::Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | Description | Define the archive action when there is a change on the interlock state. Archive if: Old/New Comparison: value changes
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | Usage | This archive mode is used to archive alarm output state in the PVSS database
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | DependentAttributes
SCADADeviceDataArchiving | Interlock Archiving::Archive Mode | Constraints | No, or Old/New Comparison
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | Description | Archive mode of MV and SP. Archive if: Old/New Comparison: value changes Time: value changes after the specified Time Filter Deadband: value < or > specified deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | DependentAttributes | If "Time" is selected, "MV and SP Archiving.Time Filter (s)" must be filled If "Deadband" is selected: "MV and SP Archiving.Deadband Type" and "MV and SP Archiving.Deadband Value" must be filled.
SCADADeviceDataArchiving | MV and SP Archiving::Archive Mode | Constraints
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of Controller MV and SP
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | Usage
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as "MV and SP Archiving.Archive Mode"
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Type | Constraints
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | Description | Deadband value for the SCADA archiving of Controller MV and SP. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | Usage
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as "MV and SP Archiving.Archive Mode"
SCADADeviceDataArchiving | MV and SP Archiving::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | Description | Time filter for the SCADA archiving of Controller MV and SP. Must be positive.
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | Usage
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as "MV and SP Archiving.Archive Mode"
SCADADeviceDataArchiving | MV and SP Archiving::Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Modes::Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes
SCADADeviceDataArchiving | Modes::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Modes::Archive Mode | DependentAttributes
SCADADeviceDataArchiving | Modes::Archive Mode | Constraints
SCADADeviceDataArchiving | Output Archiving::Archive Mode | Description | Archive mode of Output. Archive if: Old/New Comparison: value changes Time: value changes after the specified Time Filter Deadband: value < or > specified deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Output Archiving::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Output Archiving::Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Output Archiving::Archive Mode | Constraints
SCADADeviceDataArchiving | Output Archiving::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of Controller Output
SCADADeviceDataArchiving | Output Archiving::Deadband Type | Usage
SCADADeviceDataArchiving | Output Archiving::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as "Output Archiving.Archive Mode"
SCADADeviceDataArchiving | Output Archiving::Deadband Type | Constraints
SCADADeviceDataArchiving | Output Archiving::Deadband Value | Description | Deadband value for the SCADA archiving of Controller Output. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Output Archiving::Deadband Value | Usage
SCADADeviceDataArchiving | Output Archiving::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as "Output Archiving.Archive Mode"
SCADADeviceDataArchiving | Output Archiving::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | Description | Time filter for the SCADA archiving of Controller Output. Must be positive.
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | Usage
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as "Output Archiving.Archive Mode"
SCADADeviceDataArchiving | Output Archiving::Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object. Must be positive.
SCADADeviceDataArchiving | Time Filter (s) | Usage
SCADADeviceDataArchiving | Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Time Filter (s) | Constraints | Must be positive
SCADADeviceDataArchiving | Totalizer::Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Totalizer::Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Totalizer::Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Totalizer::Archive Mode | Constraints
SCADADeviceDataArchiving | Totalizer::Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the Totalizer value.
SCADADeviceDataArchiving | Totalizer::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Totalizer::Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Totalizer::Deadband Type | Constraints
SCADADeviceDataArchiving | Totalizer::Deadband Value | Description | Deadband value for the SCADA archiving of the Totalizer value. Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Totalizer::Deadband Value | Usage
SCADADeviceDataArchiving | Totalizer::Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Totalizer::Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband).
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | Usage
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Totalizer::Time Filter (s) | Constraints | Must be positive
SCADADeviceFunctionals | Access Control Domain | Description | Define Access Control on the device to an existing SCADA Domain Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | Access Control Domain | Usage | This domain is used to grant access to this specific device. The domain specified for this object will allow access to the object only to registered users on that domain
SCADADeviceFunctionals | Access Control Domain | DependentAttributes
SCADADeviceFunctionals | Access Control Domain | Constraints | Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | Mask Event | Description | If TRUE: the events of the device will be masked in SCADA and not diplayed or archived in the Event List. An 'event' is defined as a bit change in StsReg01 or StsReg02
SCADADeviceFunctionals | Mask Event | Usage
SCADADeviceFunctionals | Mask Event | DependentAttributes
SCADADeviceFunctionals | Mask Event | Constraints
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 1 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 2 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 3 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 4 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 5 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 6 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 7 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | Description | Label assigned to the option mode and displayed on the PCO widget in SCADA. Should be <= 16 characters to be correctly displayed in PCO widget.
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | Usage
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | DependentAttributes
SCADADeviceFunctionals | Mode Label::Option Mode 8 Label | Constraints | Should be <= 16 characters to be correctly displayed in PCO widget
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Description | Define links to other devices (separate device names with commas). Note: it is not necessary to link to master, parents or children because these links are automatically created. Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Usage | Linked devices will be shown in the device right-click menu
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | DependentAttributes | Expert Name or Name. The name of the device(s) specified here *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified here corresponds to "Name".
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Constraints | Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Description | Domain of the device. If empty, the domain will be the name of the application Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Usage | Domain is used to filter the devices in the alarm list or in the device tree overview
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | DependentAttributes
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Description | Nature of the device. If empty, the nature will be the type of the device Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Usage | Nature is used to filter the devices in the alarm list or in the device tree overview
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | DependentAttributes
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | Calibration::Gas Name | Description | Fluid name used to calibrate the device, to be displayed in SCADA.
SCADADeviceGraphics | Calibration::Gas Name | Usage
SCADADeviceGraphics | Calibration::Gas Name | DependentAttributes
SCADADeviceGraphics | Calibration::Gas Name | Constraints
SCADADeviceGraphics | Calibration::Unit | Description | Physical measurement unit selected by the manufacturer of the hardware device during the calibration, to be displayed in SCADA.
SCADADeviceGraphics | Calibration::Unit | Usage | This is the physical unit used by the manufacturer to calibrate the device
SCADADeviceGraphics | Calibration::Unit | DependentAttributes
SCADADeviceGraphics | Calibration::Unit | Constraints
SCADADeviceGraphics | CurveName::CC0 | Description | Fluid name associated with calibration curve 0, to be displayed in SCADA. Cannot be null/empty (there must be at least one fluid).
SCADADeviceGraphics | CurveName::CC0 | Usage
SCADADeviceGraphics | CurveName::CC0 | DependentAttributes
SCADADeviceGraphics | CurveName::CC0 | Constraints | Cannot be null/empty (there must be at least one fluid)
SCADADeviceGraphics | CurveName::CC1 | Description | Fluid name associated with calibration curve 1, to be displayed in SCADA. Can be null/empty.
SCADADeviceGraphics | CurveName::CC1 | Usage
SCADADeviceGraphics | CurveName::CC1 | DependentAttributes
SCADADeviceGraphics | CurveName::CC1 | Constraints | Can be null/empty.
SCADADeviceGraphics | CurveName::CC2 | Description | Fluid name associated with calibration curve 2, to be displayed in SCADA. Can be null/empty.
SCADADeviceGraphics | CurveName::CC2 | Usage
SCADADeviceGraphics | CurveName::CC2 | DependentAttributes
SCADADeviceGraphics | CurveName::CC2 | Constraints | Can be null/empty.
SCADADeviceGraphics | Diagnostic | Description | Define link between the device and an existing diagnostic panel for the device. The panel specified here can be accessed from the device right-click menu item "Diagnostic" as well as from the "Diagnostic" button on the object faceplate.
SCADADeviceGraphics | Diagnostic | Usage | Specify the path of the .pnl file under the "\panel" directory of the PVSS project
SCADADeviceGraphics | Diagnostic | DependentAttributes
SCADADeviceGraphics | Diagnostic | Constraints
SCADADeviceGraphics | Display Name | Description | Short Name displayed in the PCO widget in SCADA. Should be <= 8 characters to be correctly displayed in PCO widget.
SCADADeviceGraphics | Display Name | Usage
SCADADeviceGraphics | Display Name | DependentAttributes
SCADADeviceGraphics | Display Name | Constraints | Should be <= 8 characters to be correctly displayed in PCO widget
SCADADeviceGraphics | Flow::Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Flow::Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Flow::Format | DependentAttributes
SCADADeviceGraphics | Flow::Format | Constraints
SCADADeviceGraphics | Flow::Unit | Description | Physical measurement unit associated with the set point and flow, to be displayed in SCADA.
SCADADeviceGraphics | Flow::Unit | Usage
SCADADeviceGraphics | Flow::Unit | DependentAttributes
SCADADeviceGraphics | Flow::Unit | Constraints
SCADADeviceGraphics | Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Format | DependentAttributes
SCADADeviceGraphics | Format | Constraints
SCADADeviceGraphics | Label Off | Description | SCADA description associated to the State of the object
SCADADeviceGraphics | Label Off | Usage
SCADADeviceGraphics | Label Off | DependentAttributes
SCADADeviceGraphics | Label Off | Constraints
SCADADeviceGraphics | Label On | Description | SCADA description associated to the State of the object
SCADADeviceGraphics | Label On | Usage
SCADADeviceGraphics | Label On | DependentAttributes
SCADADeviceGraphics | Label On | Constraints
SCADADeviceGraphics | Pattern | Description | List of individual messages associated with the value of the object. Strict format: "Nbr=Message,Nbr=Message". The message CAN contain a space.
SCADADeviceGraphics | Pattern | Usage | When not empty, the message corresponding to the value is displayed on the panel.
SCADADeviceGraphics | Pattern | DependentAttributes
SCADADeviceGraphics | Pattern | Constraints | Strict format: "Nbr=Message,Nbr=Message". The message CAN contain a space.
SCADADeviceGraphics | Synoptic | Description | Define link between the device and an existing synoptic where it appears. The synoptic specified here can be accessed from the device right-click menu item "Synoptic".
SCADADeviceGraphics | Synoptic | Usage | Specify the path of the .pnl file under the "\panel" directory of the PVSS project.
SCADADeviceGraphics | Synoptic | DependentAttributes
SCADADeviceGraphics | Synoptic | Constraints
SCADADeviceGraphics | Totalizer::Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Totalizer::Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Totalizer::Format | DependentAttributes
SCADADeviceGraphics | Totalizer::Format | Constraints
SCADADeviceGraphics | Totalizer::Unit | Description | Physical measurement unit associated with the fluid totalizer value, to be displayed in SCADA.
SCADADeviceGraphics | Totalizer::Unit | Usage
SCADADeviceGraphics | Totalizer::Unit | DependentAttributes
SCADADeviceGraphics | Totalizer::Unit | Constraints
SCADADeviceGraphics | Unit | Description | Unit of the device to be displayed in SCADA
SCADADeviceGraphics | Unit | Usage
SCADADeviceGraphics | Unit | DependentAttributes
SCADADeviceGraphics | Unit | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | WWW Link | Description | Define link between the device and an existing web page (or pdf file, or other file which can be opened with IE). The link can be accessed from the device right-click menu item "Info" as well as from the "Info" button on the object faceplate.
SCADADeviceGraphics | WWW Link | Usage
SCADADeviceGraphics | WWW Link | DependentAttributes
SCADADeviceGraphics | WWW Link | Constraints
SCADADeviceGraphics | Widget Type | Description | Define the widget type to display in the SCADA device tree overview only. The widget displayed in the process panel will be selected when the user creates the panel.
SCADADeviceGraphics | Widget Type | Usage
SCADADeviceGraphics | Widget Type | DependentAttributes
SCADADeviceGraphics | Widget Type | Constraints
SCADADeviceParameters | F Range Max | Description | Floating value corresponding to the Maximal Range.
SCADADeviceParameters | F Range Max | Usage | When the Widget Type is "Word2AnalogStatus" the word value will be converted at the level of the SCADA into a Float number .
SCADADeviceParameters | F Range Max | DependentAttributes | Widget Type
SCADADeviceParameters | F Range Max | Constraints | Must be present when the Widget Type is "Word2AnalogStatus"
SCADADeviceParameters | F Range Min | Description | Floating value corresponding to the Minimal Range. Must be present when the Widget Type is "Word2AnalogStatus".
SCADADeviceParameters | F Range Min | Usage | When the Widget Type is "Word2AnalogStatus" the word value will be converted at the level of the SCADA into a Float number .
SCADADeviceParameters | F Range Min | DependentAttributes | Widget Type
SCADADeviceParameters | F Range Min | Constraints | Must be present when the Widget Type is "Word2AnalogStatus".
SCADADriverDataSmoothing | Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband)
SCADADriverDataSmoothing | Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Deadband Type | Constraints
SCADADriverDataSmoothing | Deadband Value | Description | Deadband value for the SCADA driver data smoothing Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | Flow::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband) of Flow.
SCADADriverDataSmoothing | Flow::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADriverDataSmoothing | Flow::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Flow::Deadband Type | Constraints | Valid if "Deadband" has been selected as Archive Mode
SCADADriverDataSmoothing | Flow::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Flow. Must be positive and smaller than the deadband specified for the archiving.
SCADADriverDataSmoothing | Flow::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Flow::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Flow::Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing of Controller MV and SP
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Type | Constraints
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Controller MV and SP. Must be positive and smaller than the deadband specified in "MV and SP Archiving.Deadband Value"
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | MV and SP Smoothing::Deadband Value | Constraints | Must be positive and smaller than the deadband specified in "MV and SP Archiving.Deadband Value"
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband) of Controller Output
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Output Smoothing::Deadband Type | Constraints
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Controller Output. Must be positive and smaller than the deadband specified in "Output Archiving.Deadband Value"
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Output Smoothing::Deadband Value | Constraints | Must be positive and smaller than the deadband specified in "Output Archiving.Deadband Value"
SCADADriverDataSmoothing | Totalizer::Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband) of Totalizer value.
SCADADriverDataSmoothing | Totalizer::Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADriverDataSmoothing | Totalizer::Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Totalizer::Deadband Type | Constraints | Valid if "Deadband" has been selected as Archive Mode
SCADADriverDataSmoothing | Totalizer::Deadband Value | Description | Deadband value for the SCADA driver data smoothing (Driver deadband) of Totalizer value. Must be positive and smaller than the deadband specified for the archiving.
SCADADriverDataSmoothing | Totalizer::Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Totalizer::Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Totalizer::Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving

## DataValidation (hidden)
TRUE | FALSE
DigitalInput
No | Old/New Comparison
AnalogInput_Small | AnalogInput_SciOrPrecision
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
AnalogInput_Small | AnalogInput_SciOrPrecision
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Linac | Moore
AnalogInput_Small | AnalogInput_SciOrPrecision
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Information | Warning | Alarm | Safety Alarm
DigitalOutput
No | Old/New Comparison
AnalogOutput_Small | AnalogOutput_SciOrPrecision
True | False
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
AnalogOutput_Small | AnalogOutput_SciOrPrecision
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
DigitalParameter | DigitalParameterKnob
No | Old/New Comparison
WordParameter | WordParameterStat
No | Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
No | Relative | Absolute | Old/New
AnalogParameter | AnalogParameterStat | AnalogParameterWide
No | Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
No | Relative | Absolute | Old/New
WordStatus | WordStatusWide | WordStatusBit | WordStatusBitBig | WordStatusStep | WordStatusTransition | Word2AnalogStatus
No | Time | Deadband | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Absolute | Relative
No | Relative | Absolute | Old/New
AnalogStatus | AnalogStatusWide
No | Time | Deadband | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Full/Empty | Full/Half/Empty
TRUE | FALSE
LocalSquare | LocalValveHorizontal | LocalValveVertical | LocalPumpHorizontalLeft | LocalPumpHorizontalRight | LocalPumpVerticalHigh | LocalPumpVerticalLow | LocalDamperHorizontal | LocalDoubleDamperHorizontal | LocalHeaterHorizontal | LocalHeaterVertical | LocalMotor
No | Old/New Comparison
On/Open | Off/Close | 2 DO Off | 2 DO On
Full/Empty | Full/Half/Empty
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
OnOffSquare | OnOffMotor | OnOffPumpHorizontalLeft | OnOffPumpHorizontalRight | OnOffPumpVerticalHigh | OnOffPumpVerticalLow | OnOffHeaterHorizontal | OnOffHeaterVertical | OnOffValveHorizontal | OnOffValveVertical | OnOffElectricValveHorizontal | OnOffElectricValveVertical | OnOffFan | OnOffManualValveHorizontal | OnOffManualValveVertical | OnOffDamperHorizontal | OnOffDamperVertical | OnOffDoubleDamperHorizontal | OnOffDoubleDamperVertical | OnOffElecHeaterHorizontal | OnOffElecHeaterVertical | OnOffInvertedValveHorizontal | OnOff3WayValveVerticalLeftOnDown | OnOff3WayValveVerticalRightOnUp | OnOff3WayValveHorizontalDownOnLeft | OnOff3WayValveHorizontalDownOnRight | OnOff3WayValveHorizontalUpOnLeft | OnOff3WayValveHorizontalUpOnRight | OnOffKnob
Off/Close | On/Open Normal Output | On/Open Inverted Output
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
AnalogSquare | AnalogValveHorizontal | AnalogValveVertical | AnalogHeaterHorizontal | AnalogHeaterVertical | AnalogDamperHorizontal | AnalogDamperVertical | AnalogDoubleDamperHorizontal | AnalogElecHeaterHorizontal | AnalogElecHeaterVertical | AnalogFan | AnalogPumpHorizontalRight | AnalogPumpVerticalUp | Analog3WayValveHorizontalDownOnLeft | Analog3WayValveHorizontalDownOnRight | Analog3WayValveHorizontalUpOnLeft | Analog3WayValveHorizontalUpOnRight | Analog3WayValveVerticalLeftOnDown | Analog3WayValveVerticalLeftOnUp | Analog3WayValveVerticalRightOnDown | Analog3WayValveVerticalRightOnUp
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Off/Close | On/Open
Classic | Bipolar
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
AnaDigSquare | AnaDigValveHorizontal | AnaDigValveVertical | AnaDigHeaterHorizontal | AnaDigHeaterVertical
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Off/Close | On/Open
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
AnaDOSquare | AnaDOElecHeaterHorizontal | AnaDOElecHeaterVertical | AnaDOFan | AnaDOHeaterHorizontal | AnaDOPumpHorizontalLeft | AnaDOPumpHorizontalRight | AnaDOPumpVerticalDown | AnaDOPumpVerticalUp | AnaDOValveHorizontal
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
On/Open | Off/Close
TRUE | FALSE
TRUE | FALSE
TRUE | FALSE
TRUE | FALSE
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
MassFlowController
No | Old/New Comparison
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
No | Relative | Absolute | Old/New
2 End Switches + Ref. Switch | 2 End Switches with faked Ref. Switch | 2 Switches plugged into the 1STEP | No End Switches.
Potentiometer | Potentiometer (support) | Encoder
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
SteppingMotor
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
Input Scaling | Input/Output Scaling | No Scaling
Controller | ControllerSetPoint | ControllerActiveX
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
No | Relative | Absolute | Old/New
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
PCO | PCOAirHandlingUniHorizontalLeft | PCOAirHandlingUniVerticalDown | PCOAirHandlingUniVerticalUp | PCOCompressorHorizontalLeft | PCOCompressorHorizontalRight | PCOCompressorVerticalHigh | PCOCompressorVerticalLow | PCOTurbineHorizontalLeft | PCOTurbineHorizontalRight | PCOTurbineVerticalHigh | PCOTurbineVerticalLow
AL | FS | TS | SI | Multiple
DigitalAlarm
No | Old/New Comparison
Information | Warning | Alarm | Safety Alarm
AL | FS | TS | SI | Multiple
AnalogAlarm | AnalogAlarm_Analog
No | Old/New Comparison
Information | Warning | Alarm | Safety Alarm

## DigitalInput
Name | DigitalInput
Package | CPC
Object Type Family | IOObjectFamily
Description | Digital Input Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  |  | LogicDeviceDefinitions
[6 empty] | FEChannel | [15 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  | Binary State |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Alarm On State | Message | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## AnalogInput
Name | AnalogInput
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Input Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [5 empty] | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[12 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | Deadband (%) | Filtering Time (s) | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## AnalogInputReal
Name | AnalogInputReal
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Input Real Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [5 empty] | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[12 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | Deadband (%) | Filtering Time (s) | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## Encoder
Name | Encoder
Package | CPC
Object Type Family | IOObjectFamily
Description | Encoder Device
Version | 1.0
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [5 empty] | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [8 empty] | LogicDeviceDefinitions
[12 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | Deadband (%) | Encoder Type | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Level | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## DigitalOutput
Name | DigitalOutput
Package | CPC
Object Type Family | IOObjectFamily
Description | Digital Output Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  |  | LogicDeviceDefinitions
[6 empty] | FEChannel | [15 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  | Binary State |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Alarm On State | Message | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## AnalogOutput
Name | AnalogOutput
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Output Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters |  |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[10 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## AnalogOutputReal
Name | AnalogOutputReal
Package | CPC
Object Type Family | IOObjectFamily
Description | Analog Output Real Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters |  |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
[10 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Electrical Diagram | Remarks | Range Min | Range Max | Raw Min | Raw Max | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## DigitalParameter
Name | DigitalParameter
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Digital Parameter Device
Version | $LastChangedRevision: 181540 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving
SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Default Value | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive

## WordParameter
Name | WordParameter
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Word Parameter Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [6 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  |  | SCADADriverDataSmoothing
[8 empty] | FEChannel | [18 empty] | SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Range Min | Range Max | Default Value | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Pattern | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value

## AnalogParameter
Name | AnalogParameter
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Analog Parameter Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  |  | SCADADriverDataSmoothing
SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Range Min | Range Max | Default Value | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value

## WordStatus
Name | WordStatus
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Word Status Device
Version | $LastChangedRevision: 181541 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [6 empty] | SCADADeviceFunctionals |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceParameters
[7 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Range Min | Range Max | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Pattern | Synoptic | Diagnostic | WWW Link | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | F Range Min | F Range Max

## AnalogStatus
Name | AnalogStatus
Package | CPC
Object Type Family | InterfaceObjectFamily
Description | Analog Status Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing
[8 empty] | FEChannel | [16 empty] | SCADADeviceClassificationTags
Name | Expert Name | Description | Remarks | Range Min | Range Max | Filtering Time (s) | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value

## Local
Name | Local
Package | CPC
Object Type Family | FieldObjectFamily
Description | Local Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  | FEDeviceEnvironmentInputs |  | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | [9 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Remarks | Full/Empty Animation | Position Alarm | Feedback On | Feedback Off | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Message | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## OnOff
Name | OnOff
Package | CPC
Object Type Family | FieldObjectFamily
Description | OnOff Device
Version | $LastChangedRevision: 181540 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [5 empty] | FEDeviceEnvironmentInputs |  |  |  |  | FEDeviceOutputs |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | [20 empty] | SCADADeviceClassificationTags | [7 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | Full/Empty Animation | Manual Restart after Full Stop | Constant Time Pulse | Warning Time Delay (s) | Pulse Duration (s) | Feedback On | Feedback Off | Local Drive | Local On | Local Off | Process Output | Process Output Off | Widget Type | Label On | Label Off | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## Analog
Name | Analog
Package | CPC
Object Type Family | FieldObjectFamily
Description | Analog Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [7 empty] | FEDeviceManualRequests |  | FEDeviceEnvironmentInputs |  |  |  |  | FEDeviceOutputs | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [23 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | Manual Restart after Full Stop | Warning Time Delay (s) | Warning Deadband Value (Unit) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Manual Increase Step (Unit) | Manual Decrease Step (Unit) | Parameter Limit On/Open | Parameter Limit Off/Closed | Feedback Analog | Feedback On | Feedback Off | Hardware Analog Output | Local Drive | Process Output | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## AnalogDigital
Name | AnalogDigital
Package | CPC
Object Type Family | FieldObjectFamily
Description | Analog Digital Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [14 empty] | FEDeviceManualRequests |  | FEDeviceEnvironmentInputs |  |  |  |  | FEDeviceOutputs |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [11 empty] | PWM Parameters | [19 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | PWM Mode | Outputs Maintained | Manual Restart after Full Stop | Range Min | Range Max | Warning Time Delay (s) | Warning Deadband Value (Unit) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Manual Increase Step (Unit) | Manual Decrease Step (Unit) | Time Period (s) | Max Deviation | Minimum Duration (s) | Parameter Limit On/Open | Parameter Limit Off/Closed | Feedback Analog | Feedback On | Feedback Off | Hardware Analog Output | Local Drive | Output On | Output Off | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## AnaDO
Name | AnaDO
Package | CPC
Object Type Family | FieldObjectFamily
Description | Unicos TCT type for the ANADO Object Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [7 empty] | FEDeviceManualRequests |  | FEDeviceEnvironmentInputs | [5 empty] | FEDeviceOutputs |  | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [25 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Fail-Safe | Manual Restart after Full Stop | Warning Time Delay (s) | Warning Deadband Value (Unit) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Manual Increase Step (Unit) | Manual Decrease Step (Unit) | Parameter Limit On/Open | Parameter Limit Off/Closed | Feedback Analog | Feedback On | Local Drive | Hardware Analog Output | Local On | Local Off | Analog Process Output | Digital Process Output | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## MassFlowController
Name | MassFlowController
Package | CPC
Object Type Family | FieldObjectFamily
Description | Mass Flow Controller Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  |  | FEDeviceParameters | [15 empty] | FEDeviceOutputs | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [12 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [11 empty] | SCADADriverDataSmoothing |  |  |  | LogicDeviceDefinitions
[5 empty] | ParReg | [17 empty] | FEChannel | [13 empty] | CurveName |  |  | Flow |  | Calibration |  | Totalizer |  |  |  | SCADADeviceClassificationTags |  |  | Modes | Flow |  |  |  | Totalizer | [6 empty] | Flow |  | Totalizer |  |  |  | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Electrical Diagram | Remarks | Fail-Safe | Feedback Off | Inhibit Totalizer cmd | Convert ratio to Unit/time | Noise Filter | Manual Restart after Full Stop | Warning Time Delay (s) | Manual Increase Speed (Unit/s) | Manual Decrease Speed (Unit/s) | Flow Conversion | Volume Conversion | CC0 Max Flow (Unit/time) | CC1 Max Flow (Unit/time) | CC2 Max Flow (Unit/time) | Deadband (%) | Filtering Time (s) | Valve Order | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Widget Type | Synoptic | Diagnostic | WWW Link | CC0 | CC1 | CC2 | Unit | Format | Unit | Gas Name | Unit | Format | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## SteppingMotor
Name | SteppingMotor
Package | CPC
Object Type Family | FieldObjectFamily
Description | Unicos TCT type for the Stepping Motor Object Device
Version | $LastChangedRevision: 0001 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [11 empty] | FEDeviceEnvironmentInputs |  |  | FEDeviceOutputs |  |  | FEDeviceIOConfig | [10 empty] | SCADADeviceGraphics | [5 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | LogicDeviceDefinitions
|  |  |  | ParReg | [18 empty] | FEChannel | [17 empty] | SCADADeviceClassificationTags | [13 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Switches Configuration | Feedback | Manual Restart after Full Stop | Reference Position | Minimum Range | Maximum Range | Scale | Offset | Max Speed | Warning Time Delay (s) | Warning Deadband Value (Unit) | Deadband Trigger | Feedback Analog | ClockWise Limit | CounterClockWise Limit | ClockWise to Reference Switch | Simulated Reference Switch | Driver Enable | FE Encoding Type | InterfaceParam1 | InterfaceParam2 | InterfaceParam3 | InterfaceParam4 | InterfaceParam5 | InterfaceParam6 | InterfaceParam7 | InterfaceParam8 | InterfaceParam9 | InterfaceParam10 | Unit | Format | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## Controller
Name | Controller
Package | CPC
Object Type Family | ControlObjectFamily
Description | Controller Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [5 empty] | FEDeviceAutoRequests |  | FEDeviceEnvironmentInputs | FEDeviceOutputs | FEDeviceVariables | [8 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [10 empty] | SCADADriverDataSmoothing |  |  |  | LogicDeviceDefinitions
|  |  |  | Controller Parameters | [5 empty] | Default Setpoint Speed |  |  |  | Default PID Parameters | [14 empty] | SCADADeviceClassificationTags | [5 empty] | MV and SP Archiving |  |  |  | Output Archiving |  |  |  | MV and SP Smoothing |  | Output Smoothing |  |  |  | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Output Range Min | Output Range Max | MV Filter Time (s) | PID Cycle (s) | Scaling Method | RA | Increase Speed | Decrease Speed | Measured Value | Controlled Objects | Setpoint | Kc | Ti | Td | Tds | SP High Limit | SP Low Limit | Out High Limit | Out Low Limit | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Deadband Type | Deadband Value | Deadband Type | Deadband Value | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | DL User Template

## ProcessControlObject
Name | ProcessControlObject
Package | CPC
Object Type Family | ControlObjectFamily
Description | Process Control Object Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [8 empty] | SCADADeviceGraphics |  |  |  |  | SCADADeviceFunctionals | [12 empty] | SCADADeviceDataArchiving |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | Option Mode Allowance Table | [14 empty] | Mode Label | [7 empty] | SCADADeviceClassificationTags | [7 empty] | CustomLogicParameters | [9 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Manual Restart after Full Stop | Option Mode 1 Allowance | Option Mode 2 Allowance | Option Mode 3 Allowance | Option Mode 4 Allowance | Option Mode 5 Allowance | Option Mode 6 Allowance | Option Mode 7 Allowance | Option Mode 8 Allowance | Widget Type | Display Name | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Option Mode 1 Label | Option Mode 2 Label | Option Mode 3 Label | Option Mode 4 Label | Option Mode 5 Label | Option Mode 6 Label | Option Mode 7 Label | Option Mode 8 Label | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Master | External Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | IL User Template | CL User Template | BL User Template | INST User Template | GL User Template | TL User Template | SL User Template | CDOL User Template | DL User Template

## DigitalAlarm
Name | DigitalAlarm
Package | CPC
Object Type Family | ControlObjectFamily
Description | Digital Alarm Device
Version | $LastChangedRevision: 170121 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | FEDeviceAlarm |  |  | FEDeviceEnvironmentInputs | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  | LogicDeviceDefinitions
[15 empty] | SCADADeviceClassificationTags | [6 empty] | Alarm Config |  |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Remarks | Alarm Delay (s) | Type | Multiple Types | Auto Acknowledge | Input | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | SMS Category | Masked | Level | Message | Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10

## AnalogAlarm
Name | AnalogAlarm
Package | CPC
Object Type Family | ControlObjectFamily
Description | Analog Alarm Device
Version | $LastChangedRevision: 170110 $
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | FEDeviceManualRequests |  |  |  | FEDeviceAlarm |  |  |  | FEDeviceEnvironmentInputs | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADeviceAlarms |  |  |  | LogicDeviceDefinitions
[20 empty] | SCADADeviceClassificationTags | [5 empty] | Interlock Archiving | Alarm Config |  |  |  |  | CustomLogicParameters
Name | Expert Name | Description | Remarks | Alarm Delay (s) | HH Alarm | H Warning | L Warning | LL Alarm | Type | Multiple Types | Auto Acknowledge | Enable Condition | Input | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Boolean Archive | Analog Archive | Event Archive | Archive Mode | SMS Category | Masked | Level | Message | Master | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10