## ProjectDocumentation
Project Name:
Application Name:
Project Description:
Project Owner:
Spec FAQ link: | http://cern.ch/UNICOS-SpecFAQ
Object Descriptions link: | http://cern.ch/UNICOS-ObjectDescription
Spec Changes:
Date | User | Comments | Version | HTML link

## SpecDoc
AttributeFamily | AttributeName | HelpCategory | HelpDescription
DeviceDocumentation | Description | Description | Description of the device.
DeviceDocumentation | Description | Usage | Used in the SCADA layer in the device faceplate
DeviceDocumentation | Description | DependentAttributes
DeviceDocumentation | Description | Constraints | In principle there is no limit to the number of characters used, however a long description may result in display issues at the SCADA level. Forbidden characters: ;
DeviceDocumentation | Remarks | Description | Field used to add relevant information about the device.
DeviceDocumentation | Remarks | Usage | This information is not used in the generation process, it remains only at the specification level for documentation purposes.
DeviceDocumentation | Remarks | DependentAttributes
DeviceDocumentation | Remarks | Constraints | Forbidden characters: ;
DeviceIdentification | Expert Name | Description | Name of the device displayed at the SCADA level. It must be unique. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
DeviceIdentification | Expert Name | Usage | It does not affect to the datapoints names in the SCADA layer.
DeviceIdentification | Expert Name | DependentAttributes | Device Links. The name of the device(s) specified in Device Links *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified in Device Links corresponds to "Name".
DeviceIdentification | Expert Name | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦] Expert Name must be unique.
DeviceIdentification | Name | Description | Name of the device. It must be unique. Max length: - Schneider: 23 - Siemens: Field objects, Controller and PCO: 19; Local: 21; otherwise: 24 Forbidden chars: [: "'@`#$%^&*?!,;=+~(){}<>¦]-., double underscore, and page break
DeviceIdentification | Name | Usage | Name displayed at the SCADA level if "Expert Name" is not specified. This name will appear in the datapoints created in the SCADA layer.
DeviceIdentification | Name | DependentAttributes | Device Links. The name of the device(s) specified in Device Links *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified in Device Links corresponds to "Name".
DeviceIdentification | Name | Constraints | Max length: - Schneider: 23 - Siemens: Field objects, Controller and PCO: 19; Local: 21; otherwise: 24 Forbidden chars: [: "'@`#$%^&*?!,;=+~(){}<>¦]-., double underscore, and page break Name must be unique.
FEDeviceIOConfig | FEChannel::Channel | Description | TPG Channel
FEDeviceIOConfig | FEChannel::Channel | Usage
FEDeviceIOConfig | FEChannel::Channel | DependentAttributes
FEDeviceIOConfig | FEChannel::Channel | Constraints
FEDeviceIOConfig | FEChannel::DPAddr | Description | Parameter used to set up the Full Range Gauge DP Address
FEDeviceIOConfig | FEChannel::DPAddr | Usage
FEDeviceIOConfig | FEChannel::DPAddr | DependentAttributes
FEDeviceIOConfig | FEChannel::DPAddr | Constraints
FEDeviceIOConfig | FEChannel::DPFieldBusNb | Description | Parameter used to set up the fieldbus number.
FEDeviceIOConfig | FEChannel::DPFieldBusNb | Usage
FEDeviceIOConfig | FEChannel::DPFieldBusNb | DependentAttributes
FEDeviceIOConfig | FEChannel::DPFieldBusNb | Constraints
FEDeviceIOConfig | FEChannel::ErrStAddrBit | Description | Parameter used to set up the Vacuum Turbo Pump error status address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::ErrStAddrBit | Usage
FEDeviceIOConfig | FEChannel::ErrStAddrBit | DependentAttributes
FEDeviceIOConfig | FEChannel::ErrStAddrBit | Constraints
FEDeviceIOConfig | FEChannel::ErrStAddrByte | Description | Parameter used to set up the Vacuum Turbo Pump error status address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::ErrStAddrByte | Usage
FEDeviceIOConfig | FEChannel::ErrStAddrByte | DependentAttributes
FEDeviceIOConfig | FEChannel::ErrStAddrByte | Constraints
FEDeviceIOConfig | FEChannel::InputAddress | Description | Channel input address
FEDeviceIOConfig | FEChannel::InputAddress | Usage
FEDeviceIOConfig | FEChannel::InputAddress | DependentAttributes
FEDeviceIOConfig | FEChannel::InputAddress | Constraints
FEDeviceIOConfig | FEChannel::InterfaceType | Description | Define interface type used for PLC logic
FEDeviceIOConfig | FEChannel::InterfaceType | Usage
FEDeviceIOConfig | FEChannel::InterfaceType | DependentAttributes
FEDeviceIOConfig | FEChannel::InterfaceType | Constraints
FEDeviceIOConfig | FEChannel::NomStAddrBit | Description | Parameter used to set up the Vacuum Turbo Pump nominal status address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::NomStAddrBit | Usage
FEDeviceIOConfig | FEChannel::NomStAddrBit | DependentAttributes
FEDeviceIOConfig | FEChannel::NomStAddrBit | Constraints
FEDeviceIOConfig | FEChannel::NomStAddrByte | Description | Parameter used to set up the Vacuum Turbo Pump nominal status address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::NomStAddrByte | Usage
FEDeviceIOConfig | FEChannel::NomStAddrByte | DependentAttributes
FEDeviceIOConfig | FEChannel::NomStAddrByte | Constraints
FEDeviceIOConfig | FEChannel::OnDOAddrBit | Description | Parameter used to set the Full Range Gauge on output if IO interface
FEDeviceIOConfig | FEChannel::OnDOAddrBit | Usage
FEDeviceIOConfig | FEChannel::OnDOAddrBit | DependentAttributes
FEDeviceIOConfig | FEChannel::OnDOAddrBit | Constraints
FEDeviceIOConfig | FEChannel::OnDOAddrByte | Description | Parameter used to set the Full Range Gauge on output if IO interface
FEDeviceIOConfig | FEChannel::OnDOAddrByte | Usage
FEDeviceIOConfig | FEChannel::OnDOAddrByte | DependentAttributes
FEDeviceIOConfig | FEChannel::OnDOAddrByte | Constraints
FEDeviceIOConfig | FEChannel::OnDoCtrAddrBit | Description | Parameter used to set up the Vacuum Turbo Pump Controller on output address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::OnDoCtrAddrBit | Usage
FEDeviceIOConfig | FEChannel::OnDoCtrAddrBit | DependentAttributes
FEDeviceIOConfig | FEChannel::OnDoCtrAddrBit | Constraints
FEDeviceIOConfig | FEChannel::OnDoCtrAddrByte | Description | Parameter used to set up the Vacuum Turbo Pump Controller on output address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::OnDoCtrAddrByte | Usage
FEDeviceIOConfig | FEChannel::OnDoCtrAddrByte | DependentAttributes
FEDeviceIOConfig | FEChannel::OnDoCtrAddrByte | Constraints
FEDeviceIOConfig | FEChannel::OnStAddrBit | Description | Parameter used to set up the Vacuum Turbo Pump on status address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::OnStAddrBit | Usage
FEDeviceIOConfig | FEChannel::OnStAddrBit | DependentAttributes
FEDeviceIOConfig | FEChannel::OnStAddrBit | Constraints
FEDeviceIOConfig | FEChannel::OnStAddrByte | Description | Parameter used to set up the Vacuum Turbo Pump on status address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::OnStAddrByte | Usage
FEDeviceIOConfig | FEChannel::OnStAddrByte | DependentAttributes
FEDeviceIOConfig | FEChannel::OnStAddrByte | Constraints
FEDeviceIOConfig | FEChannel::OutputAddress | Description | Channel output address if DP interface
FEDeviceIOConfig | FEChannel::OutputAddress | Usage
FEDeviceIOConfig | FEChannel::OutputAddress | DependentAttributes
FEDeviceIOConfig | FEChannel::OutputAddress | Constraints
FEDeviceIOConfig | FEChannel::OutputAddressOrder | Description | Channel output address for gauge orders
FEDeviceIOConfig | FEChannel::OutputAddressOrder | Usage
FEDeviceIOConfig | FEChannel::OutputAddressOrder | DependentAttributes
FEDeviceIOConfig | FEChannel::OutputAddressOrder | Constraints
FEDeviceIOConfig | FEChannel::OutputAddressParam | Description | Channel output address for parameters
FEDeviceIOConfig | FEChannel::OutputAddressParam | Usage
FEDeviceIOConfig | FEChannel::OutputAddressParam | DependentAttributes
FEDeviceIOConfig | FEChannel::OutputAddressParam | Constraints
FEDeviceIOConfig | FEChannel::PIAddr | Description | Parameter used to set up the Vacuum Turbo Pump input peripheral base address.
FEDeviceIOConfig | FEChannel::PIAddr | Usage
FEDeviceIOConfig | FEChannel::PIAddr | DependentAttributes
FEDeviceIOConfig | FEChannel::PIAddr | Constraints
FEDeviceIOConfig | FEChannel::PQAddr | Description | Parameter used to set up the Vacuum Turbo Pump output peripheral base address.
FEDeviceIOConfig | FEChannel::PQAddr | Usage
FEDeviceIOConfig | FEChannel::PQAddr | DependentAttributes
FEDeviceIOConfig | FEChannel::PQAddr | Constraints
FEDeviceIOConfig | FEChannel::RstDOAddrBit | Description | Parameter used to set up the Vacuum Turbo Pump reset output address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::RstDOAddrBit | Usage
FEDeviceIOConfig | FEChannel::RstDOAddrBit | DependentAttributes
FEDeviceIOConfig | FEChannel::RstDOAddrBit | Constraints
FEDeviceIOConfig | FEChannel::RstDOAddrByte | Description | Parameter used to set up the Vacuum Turbo Pump reset output address if InterfaceType is 4 or 5 (IO).
FEDeviceIOConfig | FEChannel::RstDOAddrByte | Usage
FEDeviceIOConfig | FEChannel::RstDOAddrByte | DependentAttributes
FEDeviceIOConfig | FEChannel::RstDOAddrByte | Constraints
FEDeviceIOConfig | FEChannel::TMPSpeed | Description | Pump speed (Leybold Controllers)
FEDeviceIOConfig | FEChannel::TMPSpeed | Usage
FEDeviceIOConfig | FEChannel::TMPSpeed | DependentAttributes
FEDeviceIOConfig | FEChannel::TMPSpeed | Constraints
FEDeviceParameters | Default Gauge1 Gas Correction | Description | Default Gauge1 Gas Correction
FEDeviceParameters | Default Gauge1 Gas Correction | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge1 Gas Correction | DependentAttributes
FEDeviceParameters | Default Gauge1 Gas Correction | Constraints
FEDeviceParameters | Default Gauge1 Leak Comp | Description | Default Gauge1 Penning Cable Leakage Current Software compensation
FEDeviceParameters | Default Gauge1 Leak Comp | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge1 Leak Comp | DependentAttributes
FEDeviceParameters | Default Gauge1 Leak Comp | Constraints
FEDeviceParameters | Default Gauge1 Protect High Thres | Description | Default Gauge Protect High Threshold
FEDeviceParameters | Default Gauge1 Protect High Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge1 Protect High Thres | DependentAttributes
FEDeviceParameters | Default Gauge1 Protect High Thres | Constraints
FEDeviceParameters | Default Gauge1 Protect Low Thres | Description | Default Gauge1 Protect Low Threshold
FEDeviceParameters | Default Gauge1 Protect Low Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge1 Protect Low Thres | DependentAttributes
FEDeviceParameters | Default Gauge1 Protect Low Thres | Constraints
FEDeviceParameters | Default Gauge2 ATM Calibration | Description | Default Gauge2 ATM Calibration
FEDeviceParameters | Default Gauge2 ATM Calibration | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge2 ATM Calibration | DependentAttributes
FEDeviceParameters | Default Gauge2 ATM Calibration | Constraints
FEDeviceParameters | Default Gauge2 Gas Correction | Description | Default Gauge2 Gas Correction
FEDeviceParameters | Default Gauge2 Gas Correction | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge2 Gas Correction | DependentAttributes
FEDeviceParameters | Default Gauge2 Gas Correction | Constraints
FEDeviceParameters | Default Gauge2 HVac Calibration | Description | Default Gauge2 High Vac Calibration
FEDeviceParameters | Default Gauge2 HVac Calibration | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge2 HVac Calibration | DependentAttributes
FEDeviceParameters | Default Gauge2 HVac Calibration | Constraints
FEDeviceParameters | Default Gauge3 Gas Correction | Description | Default Gauge3 Gas Correction
FEDeviceParameters | Default Gauge3 Gas Correction | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge3 Gas Correction | DependentAttributes
FEDeviceParameters | Default Gauge3 Gas Correction | Constraints
FEDeviceParameters | Default Gauge3 Leak Comp | Description | Default Gauge3 Penning Cable Leakage Current Software compensation
FEDeviceParameters | Default Gauge3 Leak Comp | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge3 Leak Comp | DependentAttributes
FEDeviceParameters | Default Gauge3 Leak Comp | Constraints
FEDeviceParameters | Default Gauge3 Protect High Thres | Description | Default Gauge Protect High Threshold
FEDeviceParameters | Default Gauge3 Protect High Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge3 Protect High Thres | DependentAttributes
FEDeviceParameters | Default Gauge3 Protect High Thres | Constraints
FEDeviceParameters | Default Gauge3 Protect Low Thres | Description | Default Gauge3 Protect Low Threshold
FEDeviceParameters | Default Gauge3 Protect Low Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge3 Protect Low Thres | DependentAttributes
FEDeviceParameters | Default Gauge3 Protect Low Thres | Constraints
FEDeviceParameters | Default Gauge4 ATM Calibration | Description | Default Gauge4 ATM Calibration
FEDeviceParameters | Default Gauge4 ATM Calibration | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge4 ATM Calibration | DependentAttributes
FEDeviceParameters | Default Gauge4 ATM Calibration | Constraints
FEDeviceParameters | Default Gauge4 Gas Correction | Description | Default Gauge4 Gas Correction
FEDeviceParameters | Default Gauge4 Gas Correction | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge4 Gas Correction | DependentAttributes
FEDeviceParameters | Default Gauge4 Gas Correction | Constraints
FEDeviceParameters | Default Gauge4 HVac Calibration | Description | Default Gauge4 High Vac Calibration
FEDeviceParameters | Default Gauge4 HVac Calibration | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Gauge4 HVac Calibration | DependentAttributes
FEDeviceParameters | Default Gauge4 HVac Calibration | Constraints
FEDeviceParameters | Default Penning UR Ctr | Description | Default Penning Gauges Under Range control: 0 (UR valid), 1: (UR not valid)
FEDeviceParameters | Default Penning UR Ctr | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Penning UR Ctr | DependentAttributes
FEDeviceParameters | Default Penning UR Ctr | Constraints
FEDeviceParameters | Default Protect High Threshold | Description | Default Cold cathode Gauge Protect High Threshold status
FEDeviceParameters | Default Protect High Threshold | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Protect High Threshold | DependentAttributes
FEDeviceParameters | Default Protect High Threshold | Constraints
FEDeviceParameters | Default Protect Low Threshold | Description | Default Cold cathode Gauge Protect Low Threshold status
FEDeviceParameters | Default Protect Low Threshold | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Protect Low Threshold | DependentAttributes
FEDeviceParameters | Default Protect Low Threshold | Constraints
FEDeviceParameters | Default Rly1 High Thres | Description | Default Relay 1 High Threshold
FEDeviceParameters | Default Rly1 High Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly1 High Thres | DependentAttributes
FEDeviceParameters | Default Rly1 High Thres | Constraints
FEDeviceParameters | Default Rly1 Low Thres | Description | Default Relay 1 Low Threshold
FEDeviceParameters | Default Rly1 Low Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly1 Low Thres | DependentAttributes
FEDeviceParameters | Default Rly1 Low Thres | Constraints
FEDeviceParameters | Default Rly1 Source | Description | Default Realy 1 Source
FEDeviceParameters | Default Rly1 Source | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly1 Source | DependentAttributes
FEDeviceParameters | Default Rly1 Source | Constraints
FEDeviceParameters | Default Rly1 Timer Min OFF | Description | Relay1: Timer Minimum OFF
FEDeviceParameters | Default Rly1 Timer Min OFF | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly1 Timer Min OFF | DependentAttributes
FEDeviceParameters | Default Rly1 Timer Min OFF | Constraints
FEDeviceParameters | Default Rly2 High Thres | Description | Default Relay 2 High Threshold
FEDeviceParameters | Default Rly2 High Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly2 High Thres | DependentAttributes
FEDeviceParameters | Default Rly2 High Thres | Constraints
FEDeviceParameters | Default Rly2 Low Thres | Description | Default Relay 2 Low Threshold
FEDeviceParameters | Default Rly2 Low Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly2 Low Thres | DependentAttributes
FEDeviceParameters | Default Rly2 Low Thres | Constraints
FEDeviceParameters | Default Rly2 Source | Description | Default Realy 2 Source
FEDeviceParameters | Default Rly2 Source | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly2 Source | DependentAttributes
FEDeviceParameters | Default Rly2 Source | Constraints
FEDeviceParameters | Default Rly2 Timer Min OFF | Description | Relay2: Timer Minimum OFF
FEDeviceParameters | Default Rly2 Timer Min OFF | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly2 Timer Min OFF | DependentAttributes
FEDeviceParameters | Default Rly2 Timer Min OFF | Constraints
FEDeviceParameters | Default Rly3 High Thres | Description | Default Relay 3 High Threshold
FEDeviceParameters | Default Rly3 High Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly3 High Thres | DependentAttributes
FEDeviceParameters | Default Rly3 High Thres | Constraints
FEDeviceParameters | Default Rly3 Low Thres | Description | Default Relay 3 Low Threshold
FEDeviceParameters | Default Rly3 Low Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly3 Low Thres | DependentAttributes
FEDeviceParameters | Default Rly3 Low Thres | Constraints
FEDeviceParameters | Default Rly3 Source | Description | Default Realy 3 Source
FEDeviceParameters | Default Rly3 Source | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly3 Source | DependentAttributes
FEDeviceParameters | Default Rly3 Source | Constraints
FEDeviceParameters | Default Rly3 Timer Min OFF | Description | Relay3: Timer Minimum OFF
FEDeviceParameters | Default Rly3 Timer Min OFF | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly3 Timer Min OFF | DependentAttributes
FEDeviceParameters | Default Rly3 Timer Min OFF | Constraints
FEDeviceParameters | Default Rly4 High Thres | Description | Default Relay 4 High Threshold
FEDeviceParameters | Default Rly4 High Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly4 High Thres | DependentAttributes
FEDeviceParameters | Default Rly4 High Thres | Constraints
FEDeviceParameters | Default Rly4 Low Thres | Description | Default Relay 4 Low Threshold
FEDeviceParameters | Default Rly4 Low Thres | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly4 Low Thres | DependentAttributes
FEDeviceParameters | Default Rly4 Low Thres | Constraints
FEDeviceParameters | Default Rly4 Source | Description | Default Realy 4 Source
FEDeviceParameters | Default Rly4 Source | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly4 Source | DependentAttributes
FEDeviceParameters | Default Rly4 Source | Constraints
FEDeviceParameters | Default Rly4 Timer Min OFF | Description | Relay4: Timer Minimum OFF
FEDeviceParameters | Default Rly4 Timer Min OFF | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Default Rly4 Timer Min OFF | DependentAttributes
FEDeviceParameters | Default Rly4 Timer Min OFF | Constraints
FEDeviceParameters | Gauge1 Filter Time | Description | Default value for the gauge filter time
FEDeviceParameters | Gauge1 Filter Time | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Gauge1 Filter Time | DependentAttributes
FEDeviceParameters | Gauge1 Filter Time | Constraints
FEDeviceParameters | Gauge1 Protect Source | Description | Default value for the gauge protect source
FEDeviceParameters | Gauge1 Protect Source | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Gauge1 Protect Source | DependentAttributes
FEDeviceParameters | Gauge1 Protect Source | Constraints
FEDeviceParameters | Gauge2 Filter Time | Description | Default value for the gauge filter time
FEDeviceParameters | Gauge2 Filter Time | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Gauge2 Filter Time | DependentAttributes
FEDeviceParameters | Gauge2 Filter Time | Constraints
FEDeviceParameters | Gauge3 Filter Time | Description | Default value for the gauge filter time
FEDeviceParameters | Gauge3 Filter Time | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Gauge3 Filter Time | DependentAttributes
FEDeviceParameters | Gauge3 Filter Time | Constraints
FEDeviceParameters | Gauge3 Protect Source | Description | Default value for the gauge protect source
FEDeviceParameters | Gauge3 Protect Source | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Gauge3 Protect Source | DependentAttributes
FEDeviceParameters | Gauge3 Protect Source | Constraints
FEDeviceParameters | Gauge4 Filter Time | Description | Default value for the gauge filter time
FEDeviceParameters | Gauge4 Filter Time | Usage | This is the default parameter value assigned into the PLC variable and in the SCADA datapoint element.
FEDeviceParameters | Gauge4 Filter Time | DependentAttributes
FEDeviceParameters | Gauge4 Filter Time | Constraints
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Description | Strategy to adopt to restart the device after a Full Stop Interlock.
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Usage | FALSE: Device restarts after acknowledge. TRUE only if Full Stop disappeared: Ack+Allow Restart needed (possible only if FS disappeared) TRUE even if Full Stop still active: Ack+Allow Restart needed (possible at any moment)
FEDeviceParameters | ParReg::Manual Restart after Full Stop | DependentAttributes
FEDeviceParameters | ParReg::Manual Restart after Full Stop | Constraints | All devices of the application should have the same "Manual Restart after Full Stop"
LogicDeviceDefinitions | CustomLogicParameters::NamedListParameters | Description | Parameters to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::NamedListParameters | Usage | This parameter can be used in user logic templates to define specific logic for the device. Format is key1=value;key2=value1,value2;key2=value3 Access to values is in the format NamedListParameters[key2][1][0]
LogicDeviceDefinitions | CustomLogicParameters::NamedListParameters | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::NamedListParameters | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter1 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter10 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter2 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter3 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter4 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter5 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter6 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter7 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter8 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Description | Parameter to be used in the logic templates Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Usage | This parameter can be used in user logic templates to define specific logic for the device. If no "CustomLogicSections.* User Template"?, parameter is ignored.
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | DependentAttributes | Parameter will be used in specified "CustomLogicSections.* User Template"? file
LogicDeviceDefinitions | CustomLogicParameters::Parameter9 | Constraints | Forbidden characters: "$'
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Description | Define user template for the Dependent Logic
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Usage | Specify path of the python script located under the "UserSpecific" directory
LogicDeviceDefinitions | CustomLogicSections::DL User Template | DependentAttributes | CustomLogicParameters.ParameterX (where X=1-10)
LogicDeviceDefinitions | CustomLogicSections::DL User Template | Constraints
LogicDeviceDefinitions | External Children | Description | Children of the device are in another PLC for WinCCOA.
LogicDeviceDefinitions | External Children | Usage | The external children will appear in the hierarchy of WinCC OA
LogicDeviceDefinitions | External Children | DependentAttributes
LogicDeviceDefinitions | External Children | Constraints
LogicDeviceDefinitions | External Master | Description | Children of the device are located in another PLC for WinCCOA.
LogicDeviceDefinitions | External Master | Usage | The external master will give automatic requests to the device from another PLC. To be specified only if master is empty.
LogicDeviceDefinitions | External Master | DependentAttributes
LogicDeviceDefinitions | External Master | Constraints | Must be a single PCO for field objects, controller, or PCO.
LogicDeviceDefinitions | Gauge Controller | Description | Controller of the gauge (VR_GT)
LogicDeviceDefinitions | Gauge Controller | Usage
LogicDeviceDefinitions | Gauge Controller | DependentAttributes
LogicDeviceDefinitions | Gauge Controller | Constraints | Must be a single VR_GT device
LogicDeviceDefinitions | Master | Description | Master of the device (relative to the hierarchy of dependent objects).
LogicDeviceDefinitions | Master | Usage | The master will give automatic requests to the device. The master object will appear in the list of "Device Links" in the device right-click menu.
LogicDeviceDefinitions | Master | DependentAttributes
LogicDeviceDefinitions | Master | Constraints | Must be a single PCO for field objects, controller, or PCO. Must be PCO or field objects for alarms (several masters are allowed in the case of multiple alarms, separated by commas or spaces).
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Description | The SCADA automatically performs the alarm acknowledge
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Usage | When TRUE, the SCADA automatically acknowledges the alarm at its occurrence. The operator doesn't have to act on this alarm.
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | DependentAttributes
SCADADeviceAlarms | Alarm Config::Auto Acknowledge | Constraints | TRUE/FALSE
SCADADeviceAlarms | Alarm Config::Masked | Description | Alarm signal is ignored by the SCADA
SCADADeviceAlarms | Alarm Config::Masked | Usage | When TRUE, the Alarm signal is not recorded into the ALARM database
SCADADeviceAlarms | Alarm Config::Masked | DependentAttributes
SCADADeviceAlarms | Alarm Config::Masked | Constraints | TRUE/FALSE
SCADADeviceAlarms | Alarm Config::SMS Category | Description | This Alarm message will follow rules defined in the corresponding SMS User Group (comma-separated list)
SCADADeviceAlarms | Alarm Config::SMS Category | Usage | Defines a specific treatment for each SMS message
SCADADeviceAlarms | Alarm Config::SMS Category | DependentAttributes
SCADADeviceAlarms | Alarm Config::SMS Category | Constraints | The name must correspond to the SMS user group (unProcessAlarm,...)
SCADADeviceAlarms | Analog Thresholds::H Warning | Description | High (H) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::H Warning | Usage | Used to define an H Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::H Warning | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::H Warning | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Description | High High (HH) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Usage | Used to define an HH Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::HH Alarm | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::HH Alarm | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::L Warning | Description | Low (L) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::L Warning | Usage | Used to define an L Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::L Warning | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::L Warning | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Description | Low Low (LL) Alarm Threshold All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Usage | Used to define an LL Alarm on the sensor at SCADA level. This alarm is only used at SCADA level for information and It has no impact on the process. If empty, no alarm is created.
SCADADeviceAlarms | Analog Thresholds::LL Alarm | DependentAttributes
SCADADeviceAlarms | Analog Thresholds::LL Alarm | Constraints | All defined thresholds must be ordered (HH>H>L>LL)
SCADADeviceAlarms | Message | Description | Message to display when alarm is set in SCADA
SCADADeviceAlarms | Message | Usage | The message specified here will be displayed in the Alarm List
SCADADeviceAlarms | Message | DependentAttributes
SCADADeviceAlarms | Message | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[:"'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Analog Archive | Description | Name of the analog archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Analog Archive | Usage | The analog values of the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Analog Archive | DependentAttributes
SCADADeviceDataArchiving | Analog Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Archive Mode | Description | Archive mode of the object engineering values. Archive if: Old/New Comparison: value changes Time: value changes after Time Filter Deadband: value < or > deadband AND: at least one of the conditions is fulfilled OR: both conditions are fulfilled
SCADADeviceDataArchiving | Archive Mode | Usage | This archive mode is used to archive data in the PVSS database
SCADADeviceDataArchiving | Archive Mode | DependentAttributes | If "Time" is selected, "Time Filter (s)" must be filled If "Deadband" is selected: "Deadband Type" and "Deadband Value" must be filled.
SCADADeviceDataArchiving | Archive Mode | Constraints
SCADADeviceDataArchiving | Boolean Archive | Description | Name of the Boolean archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Boolean Archive | Usage | The boolean values of the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Boolean Archive | DependentAttributes
SCADADeviceDataArchiving | Boolean Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Deadband Type | Description | Deadband type (Relative or Absolute) of the deadband for the SCADA archiving of the engineering values of the object
SCADADeviceDataArchiving | Deadband Type | Usage | The value is archived if the difference between the latest archived value and the actual value exceeds, either: - if 'Absolute': the "Deadband Value" - if 'Relative': the "Deadband Value" as a percent of the latest archived value
SCADADeviceDataArchiving | Deadband Type | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Deadband Type | Constraints
SCADADeviceDataArchiving | Deadband Value | Description | Deadband value for the SCADA archiving of the engineering values of the object Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Deadband Value | Usage
SCADADeviceDataArchiving | Deadband Value | DependentAttributes | Valid if "Deadband" has been selected as Archive Mode
SCADADeviceDataArchiving | Deadband Value | Constraints | Must be positive and larger than the deadband specified for the driver data smoothing (Driver deadband)
SCADADeviceDataArchiving | Event Archive | Description | Name of the event archive Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Event Archive | Usage | The events generated by the device will be archived in the specified PVSS database. The archive must be created in PVSS before importing the object.
SCADADeviceDataArchiving | Event Archive | DependentAttributes
SCADADeviceDataArchiving | Event Archive | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceDataArchiving | Time Filter (s) | Description | Time filter for the SCADA archiving of the engineering values of the object. Must be positive.
SCADADeviceDataArchiving | Time Filter (s) | Usage
SCADADeviceDataArchiving | Time Filter (s) | DependentAttributes | Valid if "Time" has been selected as Archive Mode
SCADADeviceDataArchiving | Time Filter (s) | Constraints | Must be positive
SCADADeviceFunctionals | Access Control Domain | Description | Define Access Control on the device to an existing SCADA Domain Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | Access Control Domain | Usage | This domain is used to grant access to this specific device. The domain specified for this object will allow access to the object only to registered users on that domain
SCADADeviceFunctionals | Access Control Domain | DependentAttributes
SCADADeviceFunctionals | Access Control Domain | Constraints | Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | Mask Event | Description | If TRUE: the events of the device will be masked in SCADA and not diplayed or archived in the Event List. An 'event' is defined as a bit change in StsReg01 or StsReg02
SCADADeviceFunctionals | Mask Event | Usage
SCADADeviceFunctionals | Mask Event | DependentAttributes
SCADADeviceFunctionals | Mask Event | Constraints
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Description | Define links to other devices (separate device names with commas). Note: it is not necessary to link to master, parents or children because these links are automatically created. Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Usage | Linked devices will be shown in the device right-click menu
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | DependentAttributes | Expert Name or Name. The name of the device(s) specified here *must* correspond to "Expert Name" if it is defined. If "Expert Name" is not defined, the name of the device(s) specified here corresponds to "Name".
SCADADeviceFunctionals | SCADADeviceClassificationTags::Device Links | Constraints | Forbidden characters: *[: "'@`#$%^&*?!;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Description | Domain of the device. If empty, the domain will be the name of the application Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Usage | Domain is used to filter the devices in the alarm list or in the device tree overview
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | DependentAttributes
SCADADeviceFunctionals | SCADADeviceClassificationTags::Domain | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Description | Nature of the device. If empty, the nature will be the type of the device Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Usage | Nature is used to filter the devices in the alarm list or in the device tree overview
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | DependentAttributes
SCADADeviceFunctionals | SCADADeviceClassificationTags::Nature | Constraints | Forbidden characters: *[: "'@`#$%^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | Controller Model | Description | Define the controller model.
SCADADeviceGraphics | Controller Model | Usage
SCADADeviceGraphics | Controller Model | DependentAttributes
SCADADeviceGraphics | Controller Model | Constraints
SCADADeviceGraphics | Diagnostic | Description | Define link between the device and an existing diagnostic panel for the device. The panel specified here can be accessed from the device right-click menu item "Diagnostic" as well as from the "Diagnostic" button on the object faceplate.
SCADADeviceGraphics | Diagnostic | Usage | Specify the path of the .pnl file under the "\panel" directory of the PVSS project
SCADADeviceGraphics | Diagnostic | DependentAttributes
SCADADeviceGraphics | Diagnostic | Constraints
SCADADeviceGraphics | Disable | Description | Disable the gauge in SCADA (Grey color)
SCADADeviceGraphics | Disable | Usage | if TRUE, disable the gauge in SCADA (Grey color). FALSE if empty.
SCADADeviceGraphics | Disable | DependentAttributes
SCADADeviceGraphics | Disable | Constraints
SCADADeviceGraphics | Format | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | Format | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | Format | DependentAttributes
SCADADeviceGraphics | Format | Constraints
SCADADeviceGraphics | High Limit | Description | High Limit of the Gauge to display a half-filled body.
SCADADeviceGraphics | High Limit | Usage | put the high value of the gauge to display the gauge as half-filled.
SCADADeviceGraphics | High Limit | DependentAttributes
SCADADeviceGraphics | High Limit | Constraints
SCADADeviceGraphics | MotPosStFormat | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | MotPosStFormat | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | MotPosStFormat | DependentAttributes
SCADADeviceGraphics | MotPosStFormat | Constraints
SCADADeviceGraphics | MotPosStUnit | Description | Unit of the device to be displayed in SCADA
SCADADeviceGraphics | MotPosStUnit | Usage
SCADADeviceGraphics | MotPosStUnit | DependentAttributes
SCADADeviceGraphics | MotPosStUnit | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | PosStFormat | Description | Format of the value to be displayed in SCADA. Supported formats: #.## (fixed number of decimal places, in this case 2), EXP or xEXP (exponential, 3 or x digits after '.'), xD or xd (fixed digit format, x=number of digits, e.g.: 3D=0.01, 12.0, 123)
SCADADeviceGraphics | PosStFormat | Usage | Example: use format #.## to display value to 2 decimal places. To the left of the decimal point, the SCADA layer will display as many digits as required by the object value, therefore a single # is enough.
SCADADeviceGraphics | PosStFormat | DependentAttributes
SCADADeviceGraphics | PosStFormat | Constraints
SCADADeviceGraphics | PosStUnit | Description | Unit of the device to be displayed in SCADA
SCADADeviceGraphics | PosStUnit | Usage
SCADADeviceGraphics | PosStUnit | DependentAttributes
SCADADeviceGraphics | PosStUnit | Constraints | In principle there is no limit to the number of characters used, however a long name may result in display issues at the SCADA level. Forbidden characters: *[: "'@`#$^&*?!,;=+~(){}<>¦]
SCADADeviceGraphics | Synoptic | Description | Define link between the device and an existing synoptic where it appears. The synoptic specified here can be accessed from the device right-click menu item "Synoptic".
SCADADeviceGraphics | Synoptic | Usage | Specify the path of the .pnl file under the "\panel" directory of the PVSS project.
SCADADeviceGraphics | Synoptic | DependentAttributes
SCADADeviceGraphics | Synoptic | Constraints
SCADADeviceGraphics | TMP Model | Description | Define turbomolecular pump model.
SCADADeviceGraphics | TMP Model | Usage
SCADADeviceGraphics | TMP Model | DependentAttributes
SCADADeviceGraphics | TMP Model | Constraints
SCADADeviceGraphics | Under Range Validity | Description | Validity of the under range information. This is used to animate the widget. IF TRUE, under range is dark green. IF FALSE, under range is orange.
SCADADeviceGraphics | Under Range Validity | Usage | IF TRUE, widget under range is dark green. IF FALSE, widget under range is orange.
SCADADeviceGraphics | Under Range Validity | DependentAttributes
SCADADeviceGraphics | Under Range Validity | Constraints
SCADADeviceGraphics | WWW Link | Description | Define link between the device and an existing web page (or pdf file, or other file which can be opened with IE). The link can be accessed from the device right-click menu item "Info" as well as from the "Info" button on the object faceplate.
SCADADeviceGraphics | WWW Link | Usage
SCADADeviceGraphics | WWW Link | DependentAttributes
SCADADeviceGraphics | WWW Link | Constraints
SCADADeviceGraphics | Widget Type | Description | Define the widget type to display in the SCADA device tree overview only. The widget displayed in the process panel will be selected when the user creates the panel.
SCADADeviceGraphics | Widget Type | Usage
SCADADeviceGraphics | Widget Type | DependentAttributes
SCADADeviceGraphics | Widget Type | Constraints
SCADADriverDataSmoothing | Deadband Type | Description | Deadband type (None, Relative, Absolute or Old/New) for the SCADA driver data smoothing (Driver deadband)
SCADADriverDataSmoothing | Deadband Type | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Deadband Type | DependentAttributes
SCADADriverDataSmoothing | Deadband Type | Constraints
SCADADriverDataSmoothing | Deadband Value | Description | Deadband value for the SCADA driver data smoothing Must be positive and smaller than the deadband specified for the archiving
SCADADriverDataSmoothing | Deadband Value | Usage | Used for the online display in SCADA
SCADADriverDataSmoothing | Deadband Value | DependentAttributes
SCADADriverDataSmoothing | Deadband Value | Constraints | Must be positive and smaller than the deadband specified for the archiving

## DataValidation (hidden)
TRUE | FALSE
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
I/O Interface | DP Interface | Empty
VG_F | VG_F_Combined | VG_F_Analog
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
Empty | Gauge Controller Interface
A1 | A2 | B1 | B2
VG_PT_Pirani_E4 | VG_PT_Penning_E9 | VG_PT_Penning_E11
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
No | Relative | Absolute | Old/New
FALSE | TRUE only if Full Stop disappeared | TRUE even if Full Stop still active
Empty | Pfeiffer TCP350 DP | Leybold TD20-DP | Leybold iMAG-DP | IO controller STD | IO controller 2DOs
Turbovac 361 | Turbovac 1000 | Turbovac 1100 | MAG W 1300 | MAG W 1600 | MAG W 1700
TCP350 | TD20 | ACT250 | ACT600 | TC110 | DCU_TCX | Leybold iMAG
HiPace 80 | HiPace 300 | HiPace 400 | HiPace 700 | TMP 361 | TMP 800 | TMP 1000 | TMP 1100 | ATP 80 | ATP 100 | ATP 150 | ATP 400 | ATP 900 | TC110 | TPH | MAG W 1300 | MAG W 1700
VP_TP
No | Deadband | Time | Deadband AND Time | Deadband OR Time | Old/New Comparison | Old/New Comparison AND Time | Old/New Comparison OR Time
Relative | Absolute
1 | 2 | 3
1 | 2 | 3
1 | 2 | 3
1 | 2 | 3
0 | 1 | 2 | 3 | 4
0 | 1 | 2 | 3 | 4
0 | 1 | 2 | 3 | 4
0 | 1 | 2 | 3 | 4
0 | 1 | 2 | 3 | 4
0 | 1 | 2 | 3 | 4
0 | 1
Empty | Standard Interface
VR_GT
No | Old/New Comparison
No | Old/New

## VG_F
Name | VG_F
Package | Vacuum
Object Type Family | FieldObjectFamily
Description | Vacuum Gauge Full Range
Version | $LastChangedRevision: 169837 $
Default value | [32 empty] | 0.05
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters |  |  | FEDeviceIOConfig | [5 empty] | SCADADeviceGraphics | [6 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms |  |  |  |  | LogicDeviceDefinitions
|  |  |  | ParReg |  |  | FEChannel | [14 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  | CustomLogicParameters | [10 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Manual Restart after Full Stop | Default Protect High Threshold | Default Protect Low Threshold | InterfaceType | DPAddr | InputAddress | OutputAddress | OnDOAddrByte | OnDOAddrBit | Format | High Limit | Disable | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | H Warning | Master | External Master | External Children | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | NamedListParameters | DL User Template

## VG_PT
Name | VG_PT
Package | Vacuum
Object Type Family | FieldObjectFamily
Description | Vacuum Gauge Passive
Version | $LastChangedRevision$
Default value | [28 empty] | 0.05
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | FEDeviceIOConfig |  |  | SCADADeviceGraphics | [7 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADriverDataSmoothing |  | SCADADeviceAlarms |  |  |  |  | LogicDeviceDefinitions
|  |  |  | ParReg | FEChannel | [12 empty] | SCADADeviceClassificationTags | [11 empty] | Alarm Config |  |  |  | Analog Thresholds |  |  |  |  | CustomLogicParameters | [10 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Manual Restart after Full Stop | InterfaceType | Channel | InputAddress | Format | High Limit | Under Range Validity | Disable | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Deadband Value | SMS Category | Auto Acknowledge | Masked | Message | H Warning | Master | External Master | External Children | Gauge Controller | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | NamedListParameters | DL User Template

## VP_TP
Name | VP_TP
Package | Vacuum
Object Type Family | FieldObjectFamily
Description | Turbomoelecular Pump
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | FEDeviceIOConfig | [17 empty] | SCADADeviceGraphics | [9 empty] | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving | [6 empty] | SCADADeviceAlarms | [7 empty] | LogicDeviceDefinitions
|  |  |  | ParReg | FEChannel | [29 empty] | SCADADeviceClassificationTags | [9 empty] | Alarm Config |  |  |  | Analog Thresholds | [6 empty] | CustomLogicParameters | [10 empty] | CustomLogicSections
Name | Expert Name | Description | Remarks | Manual Restart after Full Stop | InterfaceType | DPAddr | DPFieldBusNb | PQAddr | PIAddr | OnStAddrByte | OnStAddrBit | ErrStAddrByte | ErrStAddrBit | NomStAddrByte | NomStAddrBit | OnDOAddrByte | OnDOAddrBit | OnDoCtrAddrByte | OnDoCtrAddrBit | RstDOAddrByte | RstDOAddrBit | TMPSpeed | PosStUnit | PosStFormat | MotPosStUnit | MotPosStFormat | Controller Model | TMP Model | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Time Filter (s) | Deadband Type | Deadband Value | Boolean Archive | Analog Archive | Event Archive | SMS Category | Auto Acknowledge | Masked | Message | HH Alarm | H Warning | L Warning | LL Alarm | Master | External Master | External Children | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | NamedListParameters | DL User Template

## VR_GT
Name | VR_GT
Package | Vacuum
Object Type Family | ControlObjectFamily
Description | Vacuum Controller - Gauge - TPG300
Version | $LastChangedRevision$
Default value
Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help | Help
DeviceIdentification |  | DeviceDocumentation |  | FEDeviceParameters | [36 empty] | FEDeviceIOConfig | [5 empty] | SCADADeviceGraphics |  |  |  | SCADADeviceFunctionals |  |  |  |  | SCADADeviceDataArchiving |  |  |  | SCADADriverDataSmoothing | LogicDeviceDefinitions
[41 empty] | FEChannel | [11 empty] | SCADADeviceClassificationTags | [7 empty] | CustomLogicParameters
Name | Expert Name | Description | Remarks | Gauge1 Filter Time | Gauge2 Filter Time | Gauge3 Filter Time | Gauge4 Filter Time | Gauge1 Protect Source | Gauge3 Protect Source | Default Rly1 Source | Default Rly2 Source | Default Rly3 Source | Default Rly4 Source | Default Gauge1 Protect High Thres | Default Gauge3 Protect High Thres | Default Rly1 High Thres | Default Rly2 High Thres | Default Rly3 High Thres | Default Rly4 High Thres | Default Gauge1 Protect Low Thres | Default Gauge3 Protect Low Thres | Default Rly1 Low Thres | Default Rly2 Low Thres | Default Rly3 Low Thres | Default Rly4 Low Thres | Default Penning UR Ctr | Default Rly1 Timer Min OFF | Default Rly2 Timer Min OFF | Default Rly3 Timer Min OFF | Default Rly4 Timer Min OFF | Default Gauge1 Leak Comp | Default Gauge3 Leak Comp | Default Gauge2 ATM Calibration | Default Gauge2 HVac Calibration | Default Gauge4 ATM Calibration | Default Gauge4 HVac Calibration | Default Gauge1 Gas Correction | Default Gauge2 Gas Correction | Default Gauge3 Gas Correction | Default Gauge4 Gas Correction | InterfaceType | DPAddr | DPFieldBusNb | InputAddress | OutputAddressParam | OutputAddressOrder | Widget Type | Synoptic | Diagnostic | WWW Link | Mask Event | Access Control Domain | Domain | Nature | Device Links | Archive Mode | Boolean Archive | Analog Archive | Event Archive | Deadband Type | Parameter1 | Parameter2 | Parameter3 | Parameter4 | Parameter5 | Parameter6 | Parameter7 | Parameter8 | Parameter9 | Parameter10 | NamedListParameters