## GasSystemSurface
ALICE TRD Gas System Surface (Profibus Adress:5)
Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0333 | 0 | FBC for PROFIBUS - Standard
0750-0430 | 1 | 8 DI 24 V DC 3.0ms
|  | 1 | E 1: Comms Test IN | 0 | 0 | 0
|  | 2 | E 2: JS0501 24V PSU Fault | 0 | 0 | 1
|  | 3 | E 3: IS0502 AC MCB Trip | 0 | 0 | 2
|  | 4 | E 4: IS0503 24V MCB Trip electr. | 0 | 0 | 3
|  | 5 | E 5: IS0504 24V MCB Trip valve | 0 | 0 | 4
|  | 6 | E 6: NU | 0 | 0 | 5
|  | 7 | E 7: NU | 0 | 0 | 6
|  | 8 | E8: YSL0515 DSS_2_GCS interlock | 0 | 0 | 7
0750-0530 | 2 | 8 DO 24 V DC 0.5A
|  | 1 | A 1: XLED0599/1 Run | 0 | 0 | 0
|  | 2 | A 2: XLED0599/2 Fill | 0 | 0 | 1
|  | 3 | A 3: XLED0599/3 Purge | 0 | 0 | 2
|  | 4 | A 4: XLED0599/4 Recuperation | 0 | 0 | 3
|  | 5 | A 5: XLED0599/5 Stop | 0 | 0 | 4
|  | 6 | A 6: XLED0599/6 Process Alarm | 0 | 0 | 5
|  | 7 | A 7: XLED0599/7 Interlock | 0 | 0 | 6
|  | 8 | A 8: XLED0599/8 PLC runing/OK | 0 | 0 | 7
0750-0530 | 3 | 8 DO 24 V DC 0.5A
|  | 1 | A 1: XLED0599/15 ELMB PLC Run Ok | 0 | 1 | 0
|  | 2 | A 2: XLED0599/12 I/O sim | 0 | 1 | 1
|  | 3 | A 3: XLED0599/11 I/O Error | 0 | 1 | 2
|  | 4 | A 4: XLED0599/9 Profibus Fault | 0 | 1 | 3
|  | 5 | A 5: XLED0599/10 CANbusFault | 0 | 1 | 4
|  | 6 | A 6: NU | 0 | 1 | 5
|  | 7 | A 7: XLED0599/13 24V PSU Fault | 0 | 1 | 6
|  | 8 | A 8: NU | 0 | 1 | 7
0750-0530 | 4 | 8 DO 24 V DC 0.5A
|  | 1 | A 1: XLED0599/17 AC MCB Trip | 0 | 2 | 0
|  | 2 | A 2: XLED0599/18 24V MCB Trip | 0 | 2 | 1
|  | 3 | A 3: NU | 0 | 2 | 2
|  | 4 | A 4: XLED0599/20 ReadyForPhysics | 0 | 2 | 3
|  | 5 | A 5: XRES0506 24V Electr.Reset | 0 | 2 | 4
|  | 6 | A 6: XRES0507 24V Valve reset | 0 | 2 | 5
|  | 7 | A 7: NU | 0 | 2 | 6
|  | 8 | A 8: Comm Test Out | 0 | 2 | 7
0750-0517 | 5 | 2 DO 230V AC 1.0A Rel 2CO (PotFree)
|  | 1 | A 1: GSY0505 ReadyForPhys.DSS | 0 | 3 | 0
|  | 2 | A 2: NU | 0 | 3 | 1
0750-0600 | 6 | End Module

## GasSystemCavern
ALICE TRD Gas System Cavern (Profibus Adress:6)
Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0333 | 0 | FBC for PROFIBUS - Standard
0750-0430 | 1 | 8 DI 24 V DC 3.0ms
|  | 1 | E 1: Comms Test IN | 5 | 0 | 0
|  | 2 | E 2: JS0601 24V PSU Fault | 5 | 0 | 1
|  | 3 | E 3: IS0602 AC MCB Trip | 5 | 0 | 2
|  | 4 | E 4: IS0603 24V MCB Trip electr. | 5 | 0 | 3
|  | 5 | E 5: IS0604 24V MCB Trip valve | 5 | 0 | 4
|  | 6 | E 6: JS0621 ELMB PSU Fault | 5 | 0 | 5
|  | 7 | E 7: Not Used = NU | 5 | 0 | 6
|  | 8 | E 8: NU | 5 | 0 | 7
0750-0530 | 2 | 8 DO 24 V DC 0.5A
|  | 1 | A 1: XLED0699/1 Run | 5 | 0 | 0
|  | 2 | A 2: XLED0699/2 Fill | 5 | 0 | 1
|  | 3 | A 3: XLED0699/3 Purge | 5 | 0 | 2
|  | 4 | A 4: XLED0699/4 Recuperation | 5 | 0 | 3
|  | 5 | A 5: XLED0699/5 Stop | 5 | 0 | 4
|  | 6 | A 6: XLED0699/6 Process Alarm | 5 | 0 | 5
|  | 7 | A 7: XLED0699/7 Interlock | 5 | 0 | 6
|  | 8 | A 8: XLED0699/8 PLC runing/OK | 5 | 0 | 7
0750-0530 | 3 | 8 DO 24 V DC 0.5A
|  | 1 | A 1: XLED0699/15 ELMB PLC Run Ok | 5 | 1 | 0
|  | 2 | A 2: XLED0699/12 I/O sim | 5 | 1 | 1
|  | 3 | A 3: XLED0699/11 I/O Error | 5 | 1 | 2
|  | 4 | A 4: XLED0699/9 Profibus Fault | 5 | 1 | 3
|  | 5 | A 5: XLED0699/10 CANbusFault | 5 | 1 | 4
|  | 6 | A 6: NU | 5 | 1 | 5
|  | 7 | A 7: XLED0699/13 24V PSU Fault | 5 | 1 | 6
|  | 8 | A 8: XLED0699/14 15VPSUfault | 5 | 1 | 7
0750-0530 | 4 | 8 DO 24 V DC 0.5A
|  | 1 | A 1: XLED0699/17 AC MCB Trip | 5 | 2 | 0
|  | 2 | A 2: XLED0699/18 24V MCB Trip | 5 | 2 | 1
|  | 3 | A 3: XLED0699/19 15V MCBTrip | 5 | 2 | 2
|  | 4 | A 4: XLED0699/20 ReadyForPhys | 5 | 2 | 3
|  | 5 | A 5: XRES0606 24V Electr.Reset | 5 | 2 | 4
|  | 6 | A 6: XRES0607 24V Valve reset | 5 | 2 | 5
|  | 7 | A 7: NU | 5 | 2 | 6
|  | 8 | A 8: Comm Test Out | 5 | 2 | 7
0750-0517 | 5 | 2 DO 230V AC 1.0A Rel 2CO (PotFree)
|  | 1 | A 1: NU | 5 | 3 | 0
|  | 2 | A 2: XRES0608 15V A Reset | 5 | 3 | 1
0750-0517 | 6 | 2 DO 230V AC 1.0A Rel 2CO (PotFree)
|  | 1 | A 1: XRES0609 15V C Reset | 5 | 4 | 0
|  | 2 | A 2: XRES0610 15V D Reset | 5 | 4 | 1
0750-0602 | 7 | 24V DC Power Supply
0750-0430 | 8 | 8 DI 24 V DC 3.0ms
|  | 1 | A 1: IS0691/1 ELMB-VA Trip 1 | 5 | 1 | 0
|  | 2 | A 2: IS0691/2 ELMB-VA Trip 2 | 5 | 1 | 1
|  | 3 | A 3: NU | 5 | 1 | 2
|  | 4 | A 4: NU | 5 | 1 | 3
|  | 5 | A 5: NU | 5 | 1 | 4
|  | 6 | A 6: NU | 5 | 1 | 5
|  | 7 | A 7: NU | 5 | 1 | 6
|  | 8 | A 8: NU | 5 | 1 | 7
0750-0602 | 9 | 24V DC Power Supply
0750-0430 | 10 | 8 DI 24 V DC 3.0ms
|  | 1 | A 1: IS0692/1 ELMB-VC Trip 1 | 5 | 2 | 0
|  | 2 | A 2: IS0692/2 ELMB-VC Trip 2 | 5 | 2 | 1
|  | 3 | A 3: IS0692/3 ELMB-VC Trip 3 | 5 | 2 | 2
|  | 4 | A 4: NU | 5 | 2 | 3
|  | 5 | A 5: NU | 5 | 2 | 4
|  | 6 | A 6: NU | 5 | 2 | 5
|  | 7 | A 7: NU | 5 | 2 | 6
|  | 8 | A 8: NU | 5 | 2 | 7
0750-0602 | 11 | 24V DC Power Supply
0750-0430 | 12 | 8 DI 24 V DC 3.0ms
|  | 1 | A 1: IS0693/1 ELMB-VD Trip 1 | 5 | 3 | 0
|  | 2 | A 2: IS0693/2 ELMB-VD Trip 2 | 5 | 3 | 1
|  | 3 | A 3: IS0693/3 ELMB-VD Trip 3 | 5 | 3 | 2
|  | 4 | A 4: NU | 5 | 3 | 3
|  | 5 | A 5: NU | 5 | 3 | 4
|  | 6 | A 6: NU | 5 | 3 | 5
|  | 7 | A 7: NU | 5 | 3 | 6
|  | 8 | A 8: NU | 5 | 3 | 7
0750-0600 | 13 | End Module

## Mixer
ALICE TOF Mixer (Profibus Adress:10)
Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0301 | 0 | Profibus DP/V1 12MBd Fieldbus Coupler
0750-0402 | 1 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: Comm Test In | 10 | 4 | 0
|  | 2 | I 2: LSH9119 (0=alarm,1=ok) | 10 | 4 | 1
|  | 3 | I 3: NU | 10 | 4 | 2
|  | 4 | I 4: NU | 10 | 4 | 3
0750-0530 | 2 | 8 DO 24 V DC 0.5A
|  | 1 | o 1: XLED 1099-2 Fill | 10 | 0 | 0
|  | 2 | o 2: XLED 1099-3 Purge | 10 | 0 | 1
|  | 3 | o 3: XLED 1099-1 Run | 10 | 0 | 2
|  | 4 | o 4: XLED 1099-4 Direct | 10 | 0 | 3
|  | 5 | o 5: XLED 1099-5 Stop | 10 | 0 | 4
|  | 6 | o 6: XLED 1099-6 Alarm | 10 | 0 | 5
|  | 7 | o 7: XLED 1099-7 Interlock | 10 | 0 | 6
|  | 8 | o 8: Comm Test Out | 10 | 0 | 7
0750-0455 | 3 | 4 AI 4-20mA s.e.
|  | 1 | I 1: PT1103 [ -1 / +3 bar] | 10 | 0 | 0
|  | 2 | I 2: PT1203 [ -1 / +3 bar] | 10 | 0 | 1
|  | 3 | I 3: PT1303 [ -1 / +3 bar] | 10 | 0 | 2
|  | 4 | I 4: PT1009 [ -1 / +3 bar] | 10 | 0 | 3
0750-0504 | 4 | 4 DO 24V DC 0.5A
|  | 1 | o 1: YV1105 (C2H2F4 LFlow) | 10 | 0 | 8
|  | 2 | o 2: YV1108 (C2H2F4 HFlow) | 10 | 0 | 9
|  | 3 | o 3: YV1205 (iC4H10 LFlow) | 10 | 0 | 10
|  | 4 | o 4: YV1208 (iC4H10 HFlow) | 10 | 0 | 11
0750-0504 | 5 | 4 DO 24V DC 0.5A
|  | 1 | o 1: YV1004 | 10 | 0 | 12
|  | 2 | o 2: YV1006 | 10 | 0 | 13
|  | 3 | o 3: YV1008 | 10 | 0 | 14
|  | 4 | o 4: YV1305 (SF6 LFlow) | 10 | 0 | 15
0750-0504 | 6 | 4 DO 24V DC 0.5A
|  | 1 | o 1: YV1308 (SF6 HFlow) | 10 | 0 | 16
|  | 2 | o 2: NU | 10 | 0 | 17
|  | 3 | o 3: NU | 10 | 0 | 18
|  | 4 | o 4: NU | 10 | 0 | 19
0750-0600 | 7 | End Module

## Purifier
ALICE TOF Purifier (Profibus Adress:20)
Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0333 | 0 | Profibus DP/V1 12MBd Fieldbus Coupler
0750-0410 | 1 | 2 DI 24 V DC 3.0ms / Proximity-Switch
|  | 1 | I 1: FIS2112 | 60 | 0 | 0
|  | 2 | I 2: FIS2212 | 60 | 0 | 1
0750-0455 | 2 | 4 AI 4-20mA s.e.
|  | 1 | I 1: FIT2109 [ 0 / 2.0 m3/h] | 60 | 1 | 0
|  | 2 | I 2: FIT2209 [ 0 / 2.0 m3/h] | 60 | 1 | 1
|  | 3 | I 3: PT2108 [ -1 / 5 bar ] | 60 | 1 | 2
|  | 4 | I 4: PT2208 [ -1 / 5 bar ] | 60 | 1 | 3
0750-0402 | 3 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: Comm test in | 60 | 5 | 0
|  | 2 | I 2: ZSL2103 (1=closed) | 60 | 5 | 1
|  | 3 | I 3: ZSH2103 (1=open) | 60 | 5 | 2
|  | 4 | I 4: ZSL2207 (1=closed) | 60 | 5 | 3
0750-0402 | 4 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: NA | 60 | 6 | 0
|  | 2 | I 2: ZSL2203 (1=closed) | 60 | 6 | 1
|  | 3 | I 3: ZSH2203 (1=open) | 60 | 6 | 2
|  | 4 | I 4: ZSH2207 (1=open) | 60 | 6 | 3
0750-0402 | 5 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: ZSL2107 (1=closed) | 60 | 7 | 0
|  | 2 | I 2: ZSH2107 (1=open) | 60 | 7 | 1
|  | 3 | I 3: XSS2101 (1=alarm) | 60 | 7 | 2
|  | 4 | I 4: XSS2201 (1=alarm) | 60 | 7 | 3
0750-0554 | 6 | 2 AO 4-20mA
|  | 1 | O 1: TZY2101 (0 / 100%) | 60 | 0 | 0
|  | 2 | O 2: TZY2201 (0 / 100%) | 60 | 0 | 1
0750-0530 | 7 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: XLED2099-1 Nominal Run | 60 | 2 | 0
|  | 2 | O 2: XLED2099-2 Single A | 60 | 2 | 1
|  | 3 | O 3: XLED2099-3 Single B | 60 | 2 | 2
|  | 4 | O 4: XLED2099-4 Double | 60 | 2 | 3
|  | 5 | O 5: XLED2099-5 Free Run | 60 | 2 | 4
|  | 6 | O 6: XLED2099-6 Stop | 60 | 2 | 5
|  | 7 | O 7: XLED2099-8 Alarm | 60 | 2 | 6
|  | 8 | O 8: XLED2099-9 Interlock | 60 | 2 | 7
0750-0530 | 8 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: XLED2199-1 Run-Cycle | 60 | 3 | 0
|  | 2 | O 2: XLED2199-2 Regen | 60 | 3 | 1
|  | 3 | O 3: XLED2199-3 Cool down | 60 | 3 | 2
|  | 4 | O 4: XLED2199-4 Standby | 60 | 3 | 3
|  | 5 | O 5: XLED2199-5 Column purge | 60 | 3 | 4
|  | 6 | O 6: XLED2199-6 Stop | 60 | 3 | 5
|  | 7 | O 7: XLED2199-8 Alarm | 60 | 3 | 6
|  | 8 | O 8: XLED2199-9 Interlock | 60 | 3 | 7
0750-0530 | 9 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: XLED2299-1 Run-Cycle | 60 | 4 | 0
|  | 2 | O 2: XLED2299-2 Regen | 60 | 4 | 1
|  | 3 | O 3: XLED2299-3 Cool Down | 60 | 4 | 2
|  | 4 | O 4: XLED2299-4 Standby | 60 | 4 | 3
|  | 5 | O 5: XLED2299-5 Column purge | 60 | 4 | 4
|  | 6 | O 6: XLED2299-6 Stop | 60 | 4 | 5
|  | 7 | O 7: XLED2299-8 Alarm | 60 | 4 | 6
|  | 8 | O 8: XLED2299-9 Interlock | 60 | 4 | 7
0750-0530 | 10 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: Comm test Out | 60 | 5 | 0
|  | 2 | O 2: NA | 60 | 5 | 1
|  | 3 | O 3: NA | 60 | 5 | 2
|  | 4 | O 4: NA | 60 | 5 | 3
|  | 5 | O 5: NA | 60 | 5 | 4
|  | 6 | O 6: NA | 60 | 5 | 5
|  | 7 | O 7: NA | 60 | 5 | 6
|  | 8 | O 8: NA | 60 | 5 | 7
0750-0460 | 11 | 4 AI PT100 (RTD)
|  | 1 | I 1: NU | 60 | 8 | 0
|  | 2 | I 2: TE2101-2 A-Outside | 60 | 8 | 1
|  | 3 | I 3: NU | 60 | 8 | 2
|  | 4 | I 4: TE2201-2 B-Outside | 60 | 8 | 3
0750-0460 | 12 | 4 AI PT100 (RTD) |  | 60
|  | 1 | I 1: TE2101-3 A-Inner-Down | 60 | 12 | 0 | TE2101-1 A-Inner-UP : The same adress as TE2101-3 due to an installation problem of SH
|  | 2 | I 2: TE2201-3 B-Inner-Down | 60 | 12 | 1 | TE2201-1 B-Inner-UP : The same adress as TE2201-3 due to an installation problem of SH
|  | 3 | I 3: NU | 60 | 12 | 2
|  | 4 | I 4: NU | 60 | 12 | 3
0750-0504 | 14 | 4 DO 24V DC 0.5A
|  | 1 | O 1: YY2001-1 (1=closed) NOpen | 60 | 6 | 0
|  | 2 | O 2: YY2001-2 (1=open) NClosed | 60 | 6 | 1
|  | 3 | O 3: YIC2005 (pump) | 60 | 6 | 2
|  | 4 | O 4: NA | 60 | 6 | 3
0750-0504 | 15 | 4 DO 24V DC 0.5A
|  | 1 | O 1: YY2103 | 60 | 7 | 0
|  | 2 | O 2: YY2107 | 60 | 7 | 1
|  | 3 | O 3: YY2110 | 60 | 7 | 2
|  | 4 | O 4: YY2111 | 60 | 7 | 3
0750-0504 | 16 | 4 DO 24V DC 0.5A
|  | 1 | O 1: YY2203 | 60 | 8 | 0
|  | 2 | O 2: YY2207 | 60 | 8 | 1
|  | 3 | O 3: YY2210 | 60 | 8 | 2
|  | 4 | O 4: YY2211 | 60 | 8 | 3
0750-0504 | 17 | 4 DO 24V DC 0.5A
|  | 1 | O 1: YY2106 | 60 | 9 | 0
|  | 2 | O 2: YY2105 | 60 | 9 | 1
|  | 3 | O 3: YY2104 | 60 | 9 | 2
|  | 4 | O 4: NU | 60 | 9 | 3
0750-0504 | 19 | 4 DO 24V DC 0.5A
|  | 1 | O 1: YY2206 | 60 | 10 | 0
|  | 2 | O 2: YY2205 | 60 | 10 | 1
|  | 3 | O 3: YY2204 | 60 | 10 | 2
|  | 4 | O 4: NU | 60 | 10 | 3
0750-0600 | 19 | End Module

## Pump
ALICE TOF Pump (Profibus Adress:40) avant 2014 | [6 empty] | ALICE TOF Pump (Profibus Adress:40) 2014
|  |  |  | Profibus Parameters | [6 empty] | Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5 | Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0333 | 0 | Profibus DP/V1 12MBd Fieldbus Coupler |  |  |  |  | 0750-0333 | 0 | Profibus DP/V1 12MBd Fieldbus Coupler
0750-0402 | 1 | 4 DI 24 V DC 3.0ms |  |  |  |  | 0750-0402 | 1 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: ComTest In | 80 | 0 | 0 |  |  | 1 | I 1: ComTest In | 80 | 0 | 0
|  | 2 | I 2: NU | 80 | 0 | 1 |  |  | 2 | I 2: NU | 80 | 0 | 1
|  | 3 | I 3: NU | 80 | 0 | 2 |  |  | 3 | I 3: NU | 80 | 0 | 2
|  | 4 | I 4: NU | 80 | 0 | 3 |  |  | 4 | I 4: NU | 80 | 0 | 3
0750-0530 | 2 | 8 DO 24 V DC 0.5A |  |  |  |  | 0750-0530 | 2 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: XLED4099/1 Run | 80 | 0 | 0 |  |  | 1 | O 1: XLED4099/1 Run | 80 | 0 | 0
|  | 2 | O 2: XLED4099/3 Starting | 80 | 0 | 1 |  |  | 2 | O 2: XLED4099/3 Starting | 80 | 0 | 1
|  | 3 | O 3: XLED4101 Pump1 On | 80 | 0 | 2 |  |  | 3 | O 3: XLED4101 Pump1 On | 80 | 0 | 2
|  | 4 | O 4: NU | 80 | 0 | 3 |  |  | 4 | O 4: XLED4201 Pump2 On | 80 | 0 | 3
|  | 5 | O 5: XLED4099/4 Stop | 80 | 0 | 4 |  |  | 5 | O 5: XLED4099/4 Stop | 80 | 0 | 4
|  | 6 | O 6: XLED4099/5 Alarm | 80 | 0 | 5 |  |  | 6 | O 6: XLED4099/5 Alarm | 80 | 0 | 5
|  | 7 | O 7: XLED4099/6 Interlock | 80 | 0 | 6 |  |  | 7 | O 7: XLED4099/6 Interlock | 80 | 0 | 6
|  | 8 | O 8: ComTest Out | 80 | 0 | 7 |  |  | 8 | O 8: ComTest Out | 80 | 0 | 7
0750-0455 | 3 | 4 AI 4-20mA s.e. |  |  |  |  | 0750-0455 | 3 | 4 AI 4-20mA s.e.
|  | 1 | I 1: PT4004 (-100 / +100 mbar) | 80 | 1 | 0 |  |  | 1 | I 1: PT4004 (-100.00 / +100.00 mbar) | 80 | 1 | 0
|  | 2 | I 2: PT4006 ( 0 / 5 bar) | 80 | 1 | 1 |  |  | 2 | I 2: PT4006 ( 0.00 / 5.00 bar) | 80 | 1 | 1
|  | 3 | I 3: PT4101/1 (0 / 5 bar) | 80 | 1 | 2 |  |  | 3 | I 3: PT4101/1 (0.0 / 5.0 bar) | 80 | 1 | 2
|  | 4 | I 4: NU | 80 | 1 | 3 |  |  | 4 | I 4: NU | 80 | 1 | 3
0750-0460 | 5 | 4 AI PT100 (RTD) |  |  |  |  | 0750-0455 | 4 | 4 AI 4-20mA s.e.
|  | 1 | I 1: TE4101/1 | 80 | 5 | 0 |  |  | 1 | I 1: PT4201/1 (0.0 / 5.0 bar) | 80 | 5 | 0
|  | 2 | I 2: NU | 80 | 5 | 1 |  |  | 2 | I 2: NU | 80 | 5 | 1
|  | 3 | I 3: NU | 80 | 5 | 2 |  |  | 3 | I 3: NU | 80 | 5 | 2
|  | 4 | I 4: NU | 80 | 5 | 3 |  |  | 4 | I 4: NU | 80 | 5 | 3
0750-0504 | 6 | 4 DO 24V DC 0.5A |  |  |  |  | 0750-0460 | 5 | 4 AI PT100 (RTD)
|  | 1 | O 1: YY4040 | 80 | 1 | 0 |  |  | 1 | I 1: TE4101/1 | 80 | 9 | 0
|  | 2 | O 2: YY4002 (normal open!!!) | 80 | 1 | 1 |  |  | 2 | I 2: NU | 80 | 9 | 1
|  | 3 | O 3: NU | 80 | 1 | 2 |  |  | 3 | I 3: TE4201/1 | 80 | 9 | 2
|  | 4 | O 4: YC4101 (Pump_1) | 80 | 1 | 3 |  |  | 4 | I 4: NU | 80 | 9 | 3
0750-0600 | 8 | End Module |  |  |  |  | 0750-0504 | 6 | 4 DO 24V DC 0.5A
[9 empty] | 1 | O 1: YY4040 | 80 | 1 | 0
[9 empty] | 2 | O 2: YY4002 (normal open!!!) | 80 | 1 | 1
[9 empty] | 3 | I 3: NU | 80 | 1 | 2
[9 empty] | 4 | O 4: YC4101 (Pump_1) | 80 | 1 | 3
[7 empty] | 0750-0504 | 7 | 4 DO 24V DC 0.5A
[9 empty] | 1 | O 1: YC4201 (Pump_2) | 80 | 2 | 0
[9 empty] | 2 | O 2: NU | 80 | 2 | 1
[9 empty] | 3 | O 3: NU | 80 | 2 | 2
[9 empty] | 4 | O 4: NU | 80 | 2 | 3
[7 empty] | 0750-0600 | 8 | End Module

## Exhaust
ALICE TOF Exhaust (Profibus Adress:50)
Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0333 | 0 | Profibus DP/V1 12MBd Fieldbus Coupler
0750-0402 | 1 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: ComTest In | 110 | 0 | 0
|  | 2 | I 2: ZSL-5003 (1=close=vent) | 110 | 0 | 1
|  | 3 | I 3: ZSH-5003 (1=open=run) | 110 | 0 | 2
|  | 4 | I 4: NU | 110 | 0 | 3
0750-0530 | 2 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: XLED5099/1 Run | 110 | 0 | 0
|  | 2 | O 2: XLED5099/2 Vent | 110 | 0 | 1
|  | 3 | O 3: NU | 110 | 0 | 2
|  | 4 | O 4: NU | 110 | 0 | 3
|  | 5 | O 5: XLED5099/3 Stop | 110 | 0 | 4
|  | 6 | O 6: XLED5099/4 Alarm | 110 | 0 | 5
|  | 7 | O 7: XLED5099/5 Interlock | 110 | 0 | 6
|  | 8 | O 8: ComTest Out | 110 | 0 | 7
0750-0455 | 3 | 4 AI 4-20mA s.e.
|  | 1 | I 1: PT5005 (0 / 5 bar) | 110 | 1 | 0
|  | 2 | I 2: PT5011 (0 / 5 bar) | 110 | 1 | 1
|  | 3 | I 3: FIT5010 ( 0 / 2 m3/h) | 110 | 1 | 2
|  | 4 | I 4: NU | 110 | 1 | 3
0750-0504 | 4 | 4 DO 24V DC 0.5A
|  | 1 | O1:YYH5003 open=run (puls!)[/1) | 110 | 1 | 0
|  | 2 | O2:YYL5003 close=vent (puls)[/2] | 110 | 1 | 1
|  | 3 | O 3: NU | 110 | 1 | 2
|  | 4 | O 4: NU | 110 | 1 | 3
0750-0600 | 5 | End Module

## Distribution Parker
ALICE TOF Distribution Parker valve definition:
Profibus number #59 |  | SH22/8/06 | Profibus Parameters
Valve name | channel number on node |  | P3 | P4 | P5
YY6123 | 0 |  | 130 | 0 | 0
YY6127 | 1 |  | 130 | 0 | 1
YY6171 | 2 |  | 130 | 0 | 2
YY6172 | 3 |  | 130 | 0 | 3
YY6223 | 4 |  | 130 | 0 | 4
YY6227 | 5 |  | 130 | 0 | 5
YY6271 | 6 |  | 130 | 0 | 6
YY6272 | 7 |  | 130 | 0 | 7
Please note: the Parker pilot valve
is always normally closed.
So: parker valve = 0 (closed=no pneumatic air to YY….)
then e.g. YV6171 = open (normal open valve)
and YV6123 = closed (normal closed valve)

## DistributionBase
ALICE TOF Distribution Base (Profibus Adress:60)
Profibus Parameters
Module | Slot | Type/Address | Description | P3 | P4 | P5
0750-0333 | 0 | Profibus DP/V1 12MBd Fieldbus Coupler
0750-0402 | 1 | 4 DI 24 V DC 3.0ms
|  | 1 | I 1: ComTest In | 161 | 0 | 0
|  | 2 | I 2: NU | 161 | 0 | 1
|  | 3 | I 3: NU | 161 | 0 | 2
|  | 4 | I 4: NU | 161 | 0 | 3
0750-0530 | 2 | 8 DO 24 V DC 0.5A
|  | 1 | O 1: XLED6099/1 Ready | 161 | 0 | 0
|  | 2 | O 2: XLED6099/2 Not Ready | 161 | 0 | 1
|  | 3 | O 3: XLED6099/3 Common Purge | 161 | 0 | 2
|  | 4 | O 4: XLED6099/4 Stop | 161 | 0 | 3
|  | 5 | O 5: XLED6099/5 Alarm | 161 | 0 | 4
|  | 6 | O 6: XLED6099/6 Interlock | 161 | 0 | 5
|  | 7 | O 7: NU | 161 | 0 | 6
|  | 8 | O 8: ComTest Out | 161 | 0 | 7
0750-0455 | 3 | 4 AI 4-20mA s.e.
|  | 1 | I 1: PT-6124 [ 0 / 40 mbar] | 161 | 1 | 0
|  | 2 | I 2: PT-6126 [-10 / +10 mbar] | 161 | 1 | 1
|  | 3 | I 3: PT-6224 [ 0 / 40 mbar] | 161 | 1 | 2
|  | 4 | I 4: PT-6226 [-10 / +10 mbar] | 161 | 1 | 3
0750-0455 | 4 | 4 AI 4-20mA s.e.
|  | 1 | I 1: PT-6104 [-10 / +10 mbar] | 161 | 5 | 0
|  | 2 | I 2: NU | 161 | 5 | 1
|  | 3 | I 3: PT-6204 [-10 / +10 mbar] | 161 | 5 | 2
|  | 4 | I 4: NU | 161 | 5 | 3
0750-0600 | 5 | End Module