## Summary
|  | FEType | Global definition
0 | No address
1 | direct access to periphery
100-199 | internal access (memory ioscanning DB, etc ..)
200-299 | Fieldbus Profibus
300-399 | Fieldbus CanOpen
400-499 | Fieldbus Ethernet-IP/ProfibusGateway-M580
Details
Step7: Siemens |  | Unity: Schneider |  | CoDeSys
FEType |  | FEType |  | FEType
0 | No address | 0 | No address | 0 | No address
1 | direct access to periphery | 1 | direct access to periphery | 1 | direct access to periphery
|  | 2 | direct access to periphery without IOSimu
…
|  | 10 | M580 Drop Quantum
100 | internal memory access | 100 | internal memory access | 100 | internal memory access
101 | Read/write: DB without IO Error | 101 | Ioscanning
102 | Read/write: DB with IO Error | 102 | Ioscanning1
103 | Read/write: DB with inverted IO Error | 103 | GlobalData
|  | 104 | GlobalData1
200 |  | 200 | Read/Write Profibus, use 401 for M580 + PRM
201 | Read/Write PA valve in Profibus DP with 10 bytes consistency check | 201 | Read/Write Profibus Byte Array, use 401 for M580 + PRM
202 | Reading from Profibus PA sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | 202 | Read/Write Profibus word Array, use 401 for M580 + PRM
203 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | 203 | Read/write Profibus Wago
204 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation) | 204 | Read/write Profibus Siemens (specific), use 401 for M580 + PRM
205 | Read/Write Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | 205 | Read/write Profibus Bronkhorst
|  | 2xx | Read/write Profibus xx
|  | 225 | Read/write via IO objects : Bronkhorst
|  | 300 | CanOpen Interface
|  | 301 | Read/write CanOpenCPP_ELMB
|  | 400 | Read/Write Ethernet IP | 400 | Read/Write EtherCat /Ethernet IP
|  | 401 | Read/Write Profibus M580 and PRM
Where XXX being a specifity of this product

## Schneider
Schneider FE Device IO Configuration
| FE_TYPE | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10
Analog Input | 0 | [10 empty] | No address
| 1 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel %IW\2.20\0.0.0.1; Schneider FE Device IO Configuration Param6: Node Status %I\2.20\0.0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError; Schneider FE Device IO Configuration Param9: RawError in % 2 | Periphery Syntax 1
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax %IW0.9.0; Schneider FE Device IO Configuration Param6: Node Status %IW0.9.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError; Schneider FE Device IO Configuration Param9: RawError in % 2 | Periphery Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: Address %I120; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | Periphery for QUANTUM Ioerror
| 2 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel %IW\2.20\0.0.0.1; Schneider FE Device IO Configuration Param6: Node Status %I\2.20\0.0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError; Schneider FE Device IO Configuration Param9: RawError in % 2 | Periphery without IOSimu
| 10 | Schneider FE Device IO Configuration Param1: Address %I120; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | M580 with Quantum DROPS with IOE
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal old syntax Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 101 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for IOScanning Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 103 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for Global Data Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 200 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 203 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - - | First address - 0 100 Card Name 2nd Part | Offset - 0 10 4 | Index - 1 5 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError | if M580 with ETH-IP - - - BMEP58 | IOType pby472 pby472 dtm Card Name 1st Part | Profibus PBY or Any DTM with Wago, card type: pby472 = 0-20mA pby474 = 4-20mA pby452 = 0-20mA pby454 = 4-20mA pby455 = 4-20mA pby468 = 0-10V pby485 = 4-20mA pby460 = 4CH PT100 pby461 = 2CH PT100 pby469 = 2 TC type K pby482/484 = 4-20mA pby472s/474s/461s = 24bits format dtm: %MW115 BMEP58(M580+ETH-IP symbols): MOD_ANA_"Param10"_"Param2".ANA_CH_IN[" Param3"].ANA.VALUE
| 204 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - 1.7.0 | First address - 0 100 0 | Offset - 0 10 0 | Index - 1 5 1 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of VFD - - - %IW1.7.0.150.8 | Other error My_IOError |  | IOType pby pby dtm pbymm420 | Same as 200 type but with one more specific case for Siemens VFD in Profibus (pbymm420)
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3]
Analog Input Real | 0 | [10 empty] | No address
| 100 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal (%MF)
| 101 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  | If M580 m580 | Same as 100 but for IoScanning, with M580: declare a Symbolic real with the address set in spec (%MW115)
| 103 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Same as 100 but for GlobalData (%MF)
| 110 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error |  |  | Internal M580 Quantum (%MF)
| 200 | Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby - dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 204 | Rack.Slot. Channel or Header or Sipart 1st Word %IW1.7.0.1 1.7.0 - %IW1.8.0.0 1.8.0 %MW10 10 | First address or Sipart 2nd Word - 0 100 %IW1.8.0.1 0 %MW11 0 | Offset - 0 10 - 0 - 0 | Index - 1 5 - 0 - 0 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of Module %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y - | Other error My_IOError |  | IOType pby pby dtm pbysipart pbysipart dtmsipart dtmsipart | Same as 200 type but with endian management and Siemens SIPART valve in Profibus (use conversion "CONV_Siemens") PBY Syntax 1 (%IW) PBY Syntax 2 (%IW) DTM Syntax (%MW) PBY Sipart Syntax 1 PBY Sipart Syntax 2 DTM Sipart Syntax 1 DTM Sipart Syntax 2
| 205 | Rack.Slot. Channel or Header or Bronkhorst 1st Word %IW1.7.0.1 1.7.0 - - - | First address or Sipart 2nd Word - 0 100 100 100 | Offset - 0 10 15 15 | Index - 1 5 - - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  |  |  | IOType pby pby dtm pbyfm dtmfm | Same as 200 type but with endian management and Bronkhorst Flowmeter in Profibus (use conversion "CONV_Siemens") PBY Syntax 1 (%IW) PBY Syntax 2 (%IW) DTM Syntax (%MW) PBY Bronk FM Syntax DTM Bronk FM Syntax
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4; Schneider FE Device IO Configuration Param7: Little Endian/Big Endian (Words) normal or inverted | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3]
Analog Output | 0 | [10 empty] | No address
| 1 | Rack.Slot. Channel 1.7.0 1.7 | First address - - | Offset - - | Index - 0 |  | Node Status %I1.7.0.ERR %I1.7.0.ERR |  | Other error My_IOError |  |  | Periphery Syntax 1 Syntax 2
| 1 | Old Syntax %QW1.7.0 | First address - | Offset - | Index - |  | Node Status %I1.7.0.ERR |  | Other error My_IOError |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: Address %MW30010; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | Periphery for QUANTUM Ioerror
| 10 | Schneider FE Device IO Configuration Param1: Address %MW30010; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | M580 with Quantum DROPS with IOE
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal old syntax Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 101 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for IOScanning Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 103 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal same as 100 but for Global Data Syntax 1: Address is Param1 Syntax2 : Address is Param2 + Param3 +Param4
| 200 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 203 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError | if M580 with ETH-IP - - - | IOType pby553 pby553 dtm | Profibus PBY or Any DTM with Wago, card type: pby553 pby555 dtm: %MW115
| 204 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - 1.7.0 | First address - 0 100 0 | Offset - 0 10 0 | Index - 1 5 1 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of VFD - - - %IW1.7.0.150.8 | Other error My_IOError |  | IOType pby pby dtm pbymm420 | Same as 200 type but with one more specific case for Siemens VFD in Profibus (pbymm420)
| 400 | Schneider FE Device IO Configuration Param1: Symbol of Card name in DTM MycardName -; Schneider FE Device IO Configuration Param2: First byte array address 0 Card Name 2nd Part; Schneider FE Device IO Configuration Param3: Offset - 0; Schneider FE Device IO Configuration Param9: EndSwitch ETC101 BMEP580301; Schneider FE Device IO Configuration Param10: IOType 553 Card Name 1st Part | Ethernet-IP with M580 + Wago I/O modules if Param9=ETC101 -> NodeSt build from Param2,Param6 and Param9, see template for more details, MOD_ANA_"Param10"_"Param2".ANA_CH_OUT[" Param3"].ANA.VALUE
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Outputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Outputs.xxxx[3]
Analog Output Real | 0 | [10 empty] | No address
| 100 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal (%MF)
| 101 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  | If M580 m580 | Same as 100 but for IoScanning, with M580: declare a Symbolic real with the address set in spec (%MW115)
| 103 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Same as 100 but for GlobalData (%MF)
| 110 | Rack.Slot. Channel or Header - | First address 100 | Offset 10 | Index 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error |  |  | Internal M580 Quantum (%MF)
| 200 | Rack.Slot. Channel or Header %QW1.7.0.1 1.7.0 - | First address - 0 100 | Offset - 0 10 | Index - 1 5 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby - dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax
| 204 | Rack.Slot. Channel or Header or Sipart 1st Word %QW1.7.0.1 1.7.0 - %QW1.8.0.0 1.8.0 %MW10 10 | First address or Sipart 2nd Word - 0 100 %QW1.8.0.1 0 %MW11 0 | Offset - 0 10 - 0 - 0 | Index - 1 5 - 0 - 0 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of Module %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxxx.y - | Other error My_IOError |  | IOType pby pby dtm pbysipart pbysipart dtmsipart dtmsipart | Same as 200 type but with endian management and Siemens SIPART valve in Profibus (use conversion "CONV_Siemens") PBY Syntax 1 (%IW) PBY Syntax 2 (%IW) DTM Syntax (%MW) PBY Sipart Syntax 1 PBY Sipart Syntax 2 DTM Sipart Syntax 1 DTM Sipart Syntax 2
| 401 | Symbol Name in Profibus DTM DP_PA_Link_IM157.Outputs.xxxx DP_PA_Link_IM157.Outputs.READBACK_POS_D_CHECKBACK_SP_OUT_1 | First Byte Array Offset 3 0 |  |  | Little Endian/Big Endian (Words) normal or inverted | Profibus Node address (for IOError) 6 | Little Endian/Big Endian (Words) normal or inverted |  |  | IOType if Sipart valve command : - sipart | Profibus Remote Module with M580 and DTM symbols Example generic: DP_PA_Link_IM157.Outputs.xxxx[3] Example with sipart Valve: DP_PA_Link_IM157.Outputs.READBACK_POS_D_CHECKBACK_SP_OUT_1[0]
Digital Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel %I0.4.0 %I\1.2.1\0.0 | First address | Offset | Index | Invert | Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR |  | Other error My_IOError |  |  | Periphery Syntax 1 Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax 0.4 \1.2.1\0; Schneider FE Device IO Configuration Param4: Index 0 0; Schneider FE Device IO Configuration Param5: Invert; Schneider FE Device IO Configuration Param6: Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError | Periphery with old syntax Syntax 1 Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel 0.2.0 5.4.0; Schneider FE Device IO Configuration Param4: Profibus/Eth-IP Node 5 -; Schneider FE Device IO Configuration Param10: IOType pby dtm or etc | Periphery with Profibus/ETH-IP and PREMIUM to detect node error on Profibus DP, dtm/etc version use CONV_FieldbusDTM pby syntax dtm syntax
| 1 | Schneider FE Device IO Configuration Param1: PRM Structure name "_PRM_Status" or -; Schneider FE Device IO Configuration Param4: Profibus Node 5; Schneider FE Device IO Configuration Param10: IOType prm ptq | Periphery with PRM and PREMIUM to detect node error on Profibus DP, use FB CONV_FieldbusDTM
| 1 | Schneider FE Device IO Configuration Param1: PRM Structure name "PRM_Gateway.Inputs" or -; Schneider FE Device IO Configuration Param4: Profibus Node 5; Schneider FE Device IO Configuration Param10: IOType prmm580 | Periphery with PRM and M580 to detect node error on Profibus DP, use CONV_FieldbusDTM
| 1 | Schneider FE Device IO Configuration Param1: Address %IW40; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | Periphery for QUANTUM Ioerror
| 10 | Schneider FE Device IO Configuration Param1: Address %IW40; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4 | M580 with Quantum DROPS with IOE
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal (%MW) Syntax 1 Syntax 2
| 200 | Rack.Slot. Channel or Header %IW1.7.0 1.7.0 - %MW115.0 | First address - 0 100 - | Offset - 0 15 - | Index - 1 0 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 201 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 203 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 400 | Symbol of Card name in DTM MycardName | First byte array address 0 | Index of bit in byte 3 |  |  | Ioerror 2 |  |  | EndSwitch ETC101 | IOType 402/430 | Ethernet IP bit stored in word array Syntax 1 Param1 + ".free0[" + Param2 + "]." + Param3
| 400 | Schneider FE Device IO Configuration Param2: Symbol of Card name in DTM Card Name 2nd Part; Schneider FE Device IO Configuration Param3: First byte array address 3; Schneider FE Device IO Configuration Param6: Ioerror 2; Schneider FE Device IO Configuration Param9: EndSwitch BMEP580301; Schneider FE Device IO Configuration Param10: IOType Card Name 1st Part | Ethernet IP bit stored in word array Syntax2 " MOD_DIS_" + Param10 + "_" + Param2 + ".DIS_CH_IN[" + Param3 + "].VALUE"
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 1; Schneider FE Device IO Configuration Param4: Index of bit in byte 4; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 5 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[1].4
Digital Output | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel %Q0.4.0 %Q1.2.1\0.0 | First address | Offset | Index | Invert | Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR |  | Other error My_IOError |  |  | Periphery Syntax 1 Syntax 2
|  | Schneider FE Device IO Configuration Param1: OldSyntax 0.4 \1.2.1\0; Schneider FE Device IO Configuration Param4: Index 0 0; Schneider FE Device IO Configuration Param5: Invert; Schneider FE Device IO Configuration Param6: Node Status %I0.4.0.ERR %I\1.2.1\0.0.ERR; Schneider FE Device IO Configuration Param8: Other error My_IOError | Periphery with old syntax Syntax 1 Syntax 2
| 1 | Schneider FE Device IO Configuration Param1: Address %M23; Schneider FE Device IO Configuration Param2: Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | Periphery for QUANTUM Ioerror
| 10 | Schneider FE Device IO Configuration Param1: Address %M23; Schneider FE Device IO Configuration Param2: M580 Quantum Drop 2; Schneider FE Device IO Configuration Param3: Quantum Slot 4; Schneider FE Device IO Configuration Param5: Drop Status Table 1st Address 216 | M580 with Quantum DROPS with IOE
| 100 | OldSyntax %MW115 - | First address - 100 | Offset - 10 | Index - 5 |  | Ioerror %MW101.5 or VAR_NAME |  | Other error My_IOError |  |  | Internal (%MW) Syntax 1 Syntax 2
| 200 | Rack.Slot. Channel or Header %QW1.7.0 1.7.0 - %MW115.0 | First address - 0 100 - | Offset - 0 15 - | Index - 1 0 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 201 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 202/203 | Rack.Slot. Channel or Header 1.7.0 1.7.0 %MW115.89 %MW115 | First address - 50 - - | Offset - 4 - - | Index 54.10 10 - 89 |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME |  | Other error My_IOError |  | IOType pby pby dtm dtm | Profibus PBY or Any DTM with Premium in an array of byte PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 204 | Rack.Slot. Channel or Header %QW1.7.0 1.7.0 - %MW115.0 | First address - 0 100 - | Offset - 0 15 - | Index - 1 0 - |  | Ioerror %IW1.7.0.1.ERR or %MW101.5 or VAR_NAME | Status of VFD %IW1.7.0.150.8 %IW1.7.0.150.8 %MWxxx.YY %MWxxx.YY | Other error My_IOError |  | IOType pbymm420 pbymm420 dtmmm420 dtmmm420 | Profibus PBY or Any DTM with Premium + Siemens VFD management, use FB CONV_Siemens PBY Syntax 1 PBY Syntax 2 DTM Syntax 1 DTM Syntax 2
| 400 | Symbol of Card name in DTM MycardName | First byte array address 0 | Index of bit in byte 3 |  |  | Ioerror 2 |  |  | EndSwitch ETC101 | IOType 504/514 /556838 | Ethernet IP bit stored in word array Syntax 1 Param1 + ".free0[" + Param2 + "]." + Param3
| 400 | Schneider FE Device IO Configuration Param2: Symbol of Card name in DTM Card Name 2nd Part; Schneider FE Device IO Configuration Param3: First byte array address 3; Schneider FE Device IO Configuration Param6: Ioerror 2; Schneider FE Device IO Configuration Param9: EndSwitch BMEP580301; Schneider FE Device IO Configuration Param10: IOType Card Name 1st Part | Ethernet IP bit stored in word array Syntax2 " MOD_DIS_" + Param10 + "_" + Param2 + ".DIS_CH_OUT[" + Param3 + "].VALUE"
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Outputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 1; Schneider FE Device IO Configuration Param4: Index of bit in byte 2; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 7 | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Outputs.xxxx[1].2
Analog Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address 200; Schneider FE Device IO Configuration Param3: Offset 10; Schneider FE Device IO Configuration Param8: If memory read -; Schneider FE Device IO Configuration Param9: If endian inversion/Normal endian/- | Internal Read memory %MF210
| 100 | Schneider FE Device IO Configuration Param2: First address 200; Schneider FE Device IO Configuration Param3: Offset 30; Schneider FE Device IO Configuration Param8: If memory write out; Schneider FE Device IO Configuration Param9: If endian inversion/Normal endian/- | Internal Write in memory %MF230
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Words) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4; Schneider FE Device IO Configuration Param7: Little Endian/Big Endian (Words) normal or inverted | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3]
Word Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address 200 %MW210; Schneider FE Device IO Configuration Param3: Offset 10; Schneider FE Device IO Configuration Param8: If memory read - - | Internal Read memory %MW210
| 100 | Schneider FE Device IO Configuration Param2: First address 200 %MW230; Schneider FE Device IO Configuration Param3: Offset 30; Schneider FE Device IO Configuration Param8: If memory write out out | Internal Write in memory %MW230
| 101 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (IOScanning PREMIUM) Channel 1-16 INT_TO_WORD(%IW" + Param1 + ".3.1)
| 102 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (IOScanning PREMIUM) Channel 16-32 INT_TO_WORD(%IW" + Param1 + ".3.2)
| 103 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (Global Data PREMIUM) Channel 1-16 INT_TO_WORD(%IW" + Param1 + ".3.9)
| 104 | Schneider FE Device IO Configuration Param1: Channel 1 | Internal (Global Data PREMIUM) Channel 16-32 INT_TO_WORD(%IW" + Param1 + ".3.10)
| 105 | Schneider FE Device IO Configuration Param2: single bits separated by ",". Put more "," for positioning VAR1,VAR2,0,VAR3 | Internal Single bit management on each Word Bit
| 200 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pby pby dtm dtm | Profibus access PBY/DTM PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 204 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pby pby dtm dtm | Profibus access PBY/DTM with lower/upper byte (endian) rotation - use for CPC5 type 10 Sipart valve checkback PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 204 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pbylowerbyte/pbylowbite pbylowerbyte/pbylowbite dtmlowerbyte/dtmbite dtmlowerbyte/dtmbite | Profibus access PBY/DTM with upper byte (big endian) deletion, use for CPC5 type 11, readback Siparrt valve PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 204 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pbyupperbyte/pbyhighbite pbyupperbyte/pbyhighbite dtmupperbyte/dtmhighbite dtmupperbyte/dtmhighbite | Profibus access PBY/DTM with lower byte (little endian) deletion, use for CPC5 type 11, readback Siparrt valve PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 205 | Schneider FE Device IO Configuration Param1: Rack.Slot. Channel or Header %IW1.7.0.1 1.7.0 - %MW115; Schneider FE Device IO Configuration Param2: First address - 0 100 -; Schneider FE Device IO Configuration Param3: Offset - 0 10 -; Schneider FE Device IO Configuration Param4: Index - 1 5 -; Schneider FE Device IO Configuration Param10: IOType pby pby dtm dtm | Profibus access PBY/DTM with lower/upper byte (endian) rotation - use for Bronkhorst Flowmeter PBY syntax 1 PBY syntax 2 DTM syntax 1 DTM syntax 2
| 401 | Schneider FE Device IO Configuration Param1: Symbol Name in Profibus DTM DP_PA_Link_IM157.Inputs.xxxx DP_PA_Link_IM157.Inputs.READBACK_POS_D_CHECKBACK_SP_IN_1; Schneider FE Device IO Configuration Param2: First Byte Array Offset 3 0; Schneider FE Device IO Configuration Param5: Little Endian/Big Endian (Bytes) normal or inverted; Schneider FE Device IO Configuration Param6: Profibus Node address (for IOError) 4; Schneider FE Device IO Configuration Param10: IOType if Sipart valve (readback only): - RD_sipart | Profibus Remote Module with M580 and DTM symbols Ex: DP_PA_Link_IM157.Inputs.xxxx[3] Example with sipart Valve: DP_PA_Link_IM157.Inputs.READBACK_POS_D_CHECKBACK_SP_IN_1[0]
Digital Parameter | 0
Word Parameter | 0
Analog Parameter | 0
| Blue field | Schneider FE Device IO Configuration Param1: Object names
| FE_TYPE | Schneider FE Device IO Configuration Param1: If empty , it is assumed to be equivalent to 0
Param1 | oldSyntax | Schneider FE Device IO Configuration Param1: The official way to specify the address is by using Param2-4 But for old spec the syntax may be in the following form: -For FE-Type1; AI: %IWR.S.C.FOI ,AO: %IQR.S.C.FOI ,DI:%I.S.C.FOI ,DO:%Q.S.C.FOI - For Type 100-103; AI,AO: %MWxx ,AIR,AOR: %MFxx ,DI,DO: %MWxxx.y
Param2,3,4 | First address, offset,index | Schneider FE Device IO Configuration Param1: Number used to build the full address : syntax %x(F+O+I) or %x(F+O).I offset, index empty are replaced by 0, First Address is mandatory.
Param5 | Invert | Schneider FE Device IO Configuration Param1: Digital Input: When "Yes" or "y", the Hfpos is inverted before the assignment to the object.
Param6 | IOerror | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %MWxxx.y - IOObjectName (posStwill be extracted) - Empty (internal variable Name_IOERROR will be declared Default: FALSE.
Param6 | NodeStatus | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %Wwxxx.y -DI object representing the decode of the IOError (Inverted)
Param8 | Other error | Schneider FE Device IO Configuration Param1: The IOError signal is either: -When Param6 is empty it is the String Param8 -When Param6 is not empty it is a OR of the two
| OUT | Schneider FE Device IO Configuration Param1: When "out" the PosSt is send to the address (F+O+I)
Param9 | endian | Schneider FE Device IO Configuration Param1: When "endian" the Big/little Endian conversion is applied.
Param9 | RawError | Schneider FE Device IO Configuration Param1: Error in percentage of the Raw Value to generate an IOError. Ex: If Param7 = 2 with a Raw values between [0 ; 10000], if the raw value is below -200 or above 10200, an IOError is generated
Param10 | "IOType" | Schneider FE Device IO Configuration Param1: Keyword specific to hardware interface. PBY or PRM plus some references of the equipment
Note on D6: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D9: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D14: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D15: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D16: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D17: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D19: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D20: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D21: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D22: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D23: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D24: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D25: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D26: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D28: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D29: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D35: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D36: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D37: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D38: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D39: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D41: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D42: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D43: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D44: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D45: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D46: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D47: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D49: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D51: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D52: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D53: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D57: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D58: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D59: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D60: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D61: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D62: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D64: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D69: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D70: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D71: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D72: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D73: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D74: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D75: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D79: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D83: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D84: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D85: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D86: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D88: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D89: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D90: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D91: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D92: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D93: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel

## Siemens
Siemens FE Device IO Configuration
| FEType | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10 | Comment | Additional Information
Analog Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PIW300 IW300; Param9: Profinet IO station; Param10: Profibus DP Slave | Reading from periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
Analog Output | 0 | [10 empty] | No address
| 1 | Param1: Perophery address PQW300 QW300; Param9: Profinet IO station; Param10: Profibus DP Slave | Direct Address | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
Digital Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address I30.0; Param9: Profinet IO station; Param10: Profibus DP Slave | Reading from periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Reading from a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with inverted IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with IO Error
Digital Output | 0 | [10 empty] | No address
| 1 | Param1: Periphery address Q30.0; Param9: Profinet IO station; Param10: Profibus DP Slave | Writing in periphery | Set in Param 9/10 the Profinet Station/DP Slave number corresponding to this device (if any) if you want to get the IO Error whenever a Profinet Station/DP Slave fault is detected
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Writing in a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with inverted IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with IO Error
Analog Input Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with inverted IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with IO Error
| 201 | Param1: Periphery address PID500 ID500 | Reading from a Profibus PA valve (in Profibus DP) with 10 bytes consistency check
| 202 | Param1: Periphery address PID500 ID500 | Reading from Profibus PA sensor (in profibus DP) with 5 bytes consistency check (4 bytes for value and 1 status byte) | The IO Error evaluation is done taking into account the consistency check and the status byte
| 203 | Param1: Periphery address PID500 ID500 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | The IO Error evaluation is done taking into account the consistency check and the status byte
| 204 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation) | The IO error of this object is always set to FALSE
| 205 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | The IO Error evaluation is based on the consistency check only.
| 206 | Param1: Periphery address PID500 ID500; Param2: Address byte of the status byte PIB504 IB504 | Reading from a Profibus DP device with 4 bytes with consistency check and status byte (4 bytes for value and 1 status byte) | The IO Error evaluation is based in the status byte and the Consistency check. The status byte address shall be defined in Param2
Analog Output Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Writing in a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with inverted IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with IO Error
| 201 | Param1: Periphery address PQD500 QD500 | Writing a Profibus PA actuator in Profibus DP with 5 bytes consistency check (4 bytes for value + 1 byte for command) | The IO Error evaluation is based on the consistency check
| 205 | Param1: Periphery address PQD500 QD500 | Writing Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | The IO Error evaluation is based on the consistency check. This type shall be semected for the Bronkhorst MFC
Analog Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PID500 ID500 | Reading from periphery | No IO Error for Analog Status objects
| 100 | Param1: M address MD30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
Word Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address in byte or word format PIW300 or PIB300 IW300 or IB300 | Reading from periphery | No IO Error for Word Status objects
| 100 | Param1: M address in byte or word format MW30 or MB30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address word or byte format 40 or DBB40 | Reading from a DB without IO Error
Word Parameter | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PQW300 QW300 | Writing in periphery | No IO Error for Word Parameter objects
| 100 | Param1: M address MW30 | Writing in M area
| 101 | Param1: Address Datablock DB30; Param2: Address word 40 | Writing in a DB without IO Error