## Summary
|  | FEType | Global definition
0 | No address
1 | direct access to periphery
100-199 | internal access (memory ioscanning DB, etc ..)
200-299 | Fieldbus Profibus
300-399 | Fieldbus CanOpen
400-499 | Fieldbus EtherCat
Details
Step7: Siemens |  | Unity: Schneider |  | CoDeSys
FEType |  | FEType |  | FEType
0 | No address | 0 | No address | 0 | No address
1 | direct access to periphery | 1 | direct access to periphery | 1 | direct access to periphery
100 | internal memory access | 100 | internal memory access | 100 | internal memory access
101 | Read/write: DB without IO Error | 101 | Ioscanning
102 | Read/write: DB with IO Error | 102 | Ioscanning1
103 | Read/write: DB with inverted IO Error | 103 | GlobalData
|  | 104 | GlobalData1
200 |  | 200 | Read/Write Profibus
201 | Read/Write PA valve in Profibus DP with 5 bytes consistency check (4 bytes for value and 1 status byte) | 201 | Read/Write Profibus Byte Array
202 | Reading from Profibus PA sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | 202 | Read/Write Profibus word Array
203 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte) | 203 | Read/write Profibus Wago
204 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation) | 204 | Read/write Profibus Siemens
205 | Read/Write Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation) | 205 | Read/write Profibus Bronkhorst
|  | 2xx | Read/write Profibus xx
|  | 300 | CanOpen Interface
|  | 301 | Read/write CanOpenCPP_ELMB
|  |  |  | 400 | Read/Write EtherCat
Where XXX being a specifity of this product

## Schneider
Schneider FE Device IO Configuration
| FE_TYPE | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10
Analog Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel | First address | Offset | Index |  | Node Status |  | Other error | RawError |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param9: RawError
| 2 | Rack.Slot.Channel | First address | Offset | Index |  | Node Status |  | Other error | RawError |  | Periphery without IOSimu
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 200 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
| 2xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error
Analog Input Real | 0 | [10 empty] | No address
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 200 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
| 3xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error
Analog Output | 0 | [10 empty] | No address
| 1 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 200 | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
| 2xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType
Analog Output Real | 0 | [10 empty] | No address
| 100 | OldSyntax | First address | Offset | Index |  | IOerror |  | Other error |  |  | Internal
| 101 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 103 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param4: Index
| 2xx | Rack.Slot. Channel | First address | Offset | Index |  | Node Status |  | Other error |  | IOType | Fieldbus
Digital Input | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param5: Invert
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error
| 100 | OldSyntax | First address | Offset | Index | Invert | IOerror |  | Other error |  |  | Internal
| 200 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType | Fieldbus
| 201 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 202 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 2xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 3xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error
Digital Output | 0 | [10 empty] | No address
| 1 | Rack.Slot.Channel | First address | Offset | Index | Invert |  |  | Other error |  |  | Periphery
| 1 | Schneider FE Device IO Configuration Param1: OldSyntax; Schneider FE Device IO Configuration Param5: Invert
| 100 | OldSyntax | First address | Offset | Index | Invert | IOerror |  | Other error |  |  | Internal
| 200 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType | Fieldbus
| 201 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 202 | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 2xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error |  | IOType
| 3xx | Rack.Slot.Channel | First address | Offset | Index | Invert | Node Status |  | Other error
Analog Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param9: endian | Internal
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param8: OUT; Schneider FE Device IO Configuration Param9: endian
Word Status | 0 | [10 empty] | No address
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset | Internal
| 100 | Schneider FE Device IO Configuration Param2: First address; Schneider FE Device IO Configuration Param3: Offset; Schneider FE Device IO Configuration Param8: OUT
| 101 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 102 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 103 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 104 | Schneider FE Device IO Configuration Param1: Rack.Slot.Channel
| 2xx | Rack.Slot.Channel | First address | Offset | Index |  | Node Status |  |  |  | IOType | Fieldbus
Digital Parameter | 0
Word Parameter | 0
Analog Parameter | 0
| Blue field | Schneider FE Device IO Configuration Param1: Object names
| FE_TYPE | Schneider FE Device IO Configuration Param1: If empty , it is assumed to be equivalent to 0
Param1 | oldSyntax | Schneider FE Device IO Configuration Param1: The official way to specify the address is by using Param2-4 But for old spec the syntax may be in the following form: -For FE-Type1; AI: %IWR.S.C.FOI ,AO: %IQR.S.C.FOI ,DI:%I.S.C.FOI ,DO:%Q.S.C.FOI - For Type 100-103; AI,AO: %MWxx ,AIR,AOR: %MFxx ,DI,DO: %MWxxx.y
Param2,3,4 | First address, offset,index | Schneider FE Device IO Configuration Param1: Number used to build the full address : syntax %x(F+O+I) or %x(F+O).I offset, index empty are replaced by 0, First Address is mandatory.
Param5 | Invert | Schneider FE Device IO Configuration Param1: When "Yes" or "y", the Hfpos is inverted before the assignment to the object.
Param6 | IOerror | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %MWxxx.y - IOObjectName (posStwill be extracted) - Empty (internal variable Name_IOERROR will be declared Default: FALSE.
Param6 | NodeStatus | Schneider FE Device IO Configuration Param1: The IOError signal is either: - %Wwxxx.y -DI object representing the decode of the IOError (Inverted)
Param8 | Other error | Schneider FE Device IO Configuration Param1: The IOError signal is either: -When Param6 is empty it is the String Param8 -When Param6 is not empty it is a OR of the two
| OUT | Schneider FE Device IO Configuration Param1: When "out" the PosSt is send to the address (F+O+I)
Param9 | endian | Schneider FE Device IO Configuration Param1: When "endian" the Big/little Endian conversion is applied.
Param9 | RawError | Schneider FE Device IO Configuration Param1: Error in percentage of the Raw Value to generate an IOError. Ex: If Param7 = 2 with a Raw values between [0 ; 10000], if the raw value is below -200 or above 10200, an IOError is generated
Param10 | "IOType" | Schneider FE Device IO Configuration Param1: Keyword specific to hardware interface. PBY or PRM plus some references of the equipment
Note on D6: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D8: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D12: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D13: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D18: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D19: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D21: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D26: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D27: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D32: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D34: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D36: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D37: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D39: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D40: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D41: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D42: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D43: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D45: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D48: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D49: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D50: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D51: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D52: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D59: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D60: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D61: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D62: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel
Note on D63: Author: The complete syntax is : Rack.Module.voie.rang.index x.x.x refer to Rack.Module.voie. Usually called as Rack.Slot.Channel

## Siemens
Siemens FE Device IO Configuration
| FEType | Param1 | Param2 | Param3 | Param4 | Param5 | Param6 | Param7 | Param8 | Param9 | Param10 | Comment
Analog Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PIW300 IW300 | Reading from periphery
Analog Output | 0 | [10 empty] | No address
| 1 | Param1: Perophery address PQW300 QW300 | Direct Address
Digital Input | 0 | [10 empty] | No address
| 1 | Param1: Periphery address I30.0 | Writing in periphery
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Reading from a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Reading from a DB with inverted IO Error
Digital Output | 0 | [10 empty] | No address
| 1 | Param1: Periphery address Q30.0 | Writing in periphery
| 101 | Param1: Address Datablock DB30; Param2: Address byte 40; Param3: Address bit 5 | Writing in a DB without IO Error
| 102 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with IO Error
| 103 | Address Datablock DB30 | Address byte 40 | Address bit 5 | Address datablock of the IO error DB50 | Address byte of the IO error 60 | Address bit of the IO error 5 |  |  |  |  | Writing in a DB with inverted IO Error
Analog Input Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Reading from a DB with inverted IO Error
| 201 | Param1: Periphery address PID500 ID500 | Reading a PA valve from Profibus DP (4 bytes for value and 1 status byte)
| 202 | Param1: Periphery address PID500 ID500 | Reading from Profibus PA sensor with 5 bytes consistency check (4 bytes for value and 1 status byte)
| 203 | Param1: Periphery address PID500 ID500 | Reading from a Standard Profibus DP sensor with 5 bytes consistency check (4 bytes for value and 1 status byte)
| 204 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device without consistency check (4 bytes for value only, no IO error evaluation)
| 205 | Param1: Periphery address PID500 ID500 | Reading from a Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation)
Analog Output Real | 0 | [10 empty] | No address
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Writing in a DB without IO Error
| 102 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with IO Error
| 103 | Param1: Address Datablock DB30; Param2: Address double word 50; Param3: Address datablock of the IO error DB50; Param4: Address byte of the IO error 60; Param5: Address bit of the IO error 5 | Writing in a DB with inverted IO Error
| 201 | Param1: Periphery address PQD500 QD500 | Writing a Profibus PA actuator in Profibus DP with 5 bytes consistency check (4 bytes for value + 1 byte for command)
| 205 | Param1: Periphery address PQD500 QD500 | Writing Profibus DP device with 4 bytes consistency check (4 bytes for value only, IO error evaluation)
Analog Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PID500 ID500 | Reading from periphery
| 100 | Param1: M address MD30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address double word 50 | Reading from a DB without IO Error
Word Status | 0 | [10 empty] | No address
| 1 | Param1: Periphery address in byte or word format PIW300 or PIB300 IW300 or IB300 | Reading from periphery
| 100 | Param1: M address in byte or word format MW30 or MB30 | Reading from M area
| 101 | Param1: Address Datablock DB30; Param2: Address word or byte format 40 or DBB40 | Reading from a DB without IO Error
Word Parameter | 0 | [10 empty] | No address
| 1 | Param1: Periphery address PQW300 QW300 | Writing in periphery
| 100 | Param1: M address MW30 | Writing in M area
| 101 | Param1: Address Datablock DB30; Param2: Address word 40 | Writing in a DB without IO Error